## Title
WATER SUPPLY SYSTEM CALCULATIONS
Project
Project number: | 1
Project version: | 1
Description: | Ada tn.3
Street:
Postal code and city:
Telephone:
Country:
Fax:
WWW:
E-mail:
Project developer
Name:
Street:
Postal code and city:
Telephone:
Country:
Fax:
WWW:
E-mail:
Designer
Name:
Street:
Postal code and city:
Telephone:
Country:
Fax:
WWW:
E-mail:
UPONOR does not accept any liability for the completeness and correctness of the calculation results and/or for all possible consequential damage which has arisen and/or which could arise from incorrect calculation.
UPONOR does not accept any liability for the completeness and correctness of the calculation results and/or for all possible consequential damage which has arisen and/or which could arise from incorrect calculation.
Info on file
File name: | C:\Documents and Settings\Kasutaja\My Documents\UNIPIPE HSE EN\Aida tn. 3 veevarustus.ISB
Creation date: | 3.06.2008
Modification date: | 17.04.2009
Printout date: | 21.04.2009

## General results
General results
No. of sources |  |  |  | 1
No. of heaters |  |  |  | 1
No. of CW and HW receptors |  |  |  | 74
No. of CW and CW pipe-runs |  |  |  | 217
incl.
No. of CW pipe-runs |  |  |  | 154
No. of HW pipe-runs |  |  |  | 63
No. of circulation circuits |  |  |  | 4
No. of circulation pipe-runs |  |  |  | 23
Total pipe network length |  |  |  | 675,7 m
incl. circulation |  |  |  | 111,2 m
Total capacity of pipe network |  |  |  | 353,8 dm³
incl. circulation |  |  |  | 13,1 dm³
Water sources
Source: no name
Source elevation: 3,5 m
Building type: Administration or office building
| Name |  |  |  | Cold water | Hot water | Circulation
| Available pressure [kPa] |  |  |  | 394.1
| Water temperature [°C] |  |  |  | 8
| Vs in source [dm3/s] [dm³/s] |  |  |  | 1.66
Pumps
| Symbol | Flow rate[dm³/s] | Pressure[kPa]
| no name | 0.09 | 12.1

## Calculations options
Calculations options
| Available pressure (Cold water) [kPa] | 0
| Available pressure (Hot water) [kPa] | 0
| Circulation pump's pressure head [kPa] | 0
| Pressure drop in circulation source [kPa] | 0
| Permissible UHW temp. drop at most remote point | 5
| Adjust hot/cold water pipes relating to specified pressure at source | Yes
| Skip to pipe successors | Yes
| Skip to pipe fitting successors | Yes

## Critical hydraulic routes
| ## | Name | Description | Unit | CW Source | HW Source
Critical hydraulic routes
Source: no name
|  | Critical path symbol |  |  | H 4
| 1 | Pressure required at source or pressure downstream of PBD or pressure controller | pminR | kPa | 394.1
| 2 | Hydrostatic head | Δphyd | kPa | 80.7
| 3 | Pressure drop on devices
|  | Water meter | ΔpWM | kPa
|  | Filter | ΔpFIL | kPa
|  | Heater | ΔpHT | kPa
|  | Remaining devices | ΔpRST | kPa
| 4 | Minimum pressure at supply point | Δpmin rec | kPa | 300
| 5 | Other pressure drops | Δpother | kPa
| 6 | Total pressure drop (no.2) to (no.5) | ΣΔp | kPa | 380.7
| 7 | Remaining pressure drop for local drops and along pipe length. Calculated as (no.1)-(no.6) | Δprst | kPa | 13.4
| 8 | Contribution from local drops |  | kPa | 6.1
| 9 | Remaining pressure drop along pipe length. Calculated as (no.7) - (no.8) |  | kPa | 7.3
| 10 | Critical path length | L | m | 48.2
| 11 | Available value of linear friction resistance. Calculated as (no.9)/(no.10) | Ravail | Pa/m | 151.34

## Receptor
| Receptor | Type | Vr [dm³/s] | Vs [dm³/s] | preq [kPa] | phydr [kPa] | Δpfp [kPa] | Δpsurp [kPa] | θinlet [°C]
Source: no name
Available pressure CW: 394,1 kPa
| H 4 | CW | 1.66 |  | 300 | 80.7 | 13.4 | 0 | 8
| H 3 | CW | 1.66 |  | 300 | 80.7 | 12.3 | 1.2 | 8
| H 3 | CW | 1.66 |  | 300 | 80.7 | 12.3 | 1.2 | 8
| H 2 | CW | 1.66 |  | 300 | 48.6 | 12.5 | 33 | 8
| H 2 | CW | 1.66 |  | 300 | 48.6 | 11.8 | 33.7 | 8
| H 1 | CW | 1.66 |  | 300 | 48.6 | 10.7 | 34.8 | 8
| Spüle | HW | 0.07 |  | 100 | 97.7 | 147.4 | 49 | 59.8
| WT | HW | 0.07 |  | 100 | 94.6 | 147.5 | 52 | 59.7
| WT | HW | 0.07 |  | 100 | 94.6 | 146.6 | 53 | 59.7
| WT | HW | 0.07 |  | 100 | 94.6 | 142.4 | 57.1 | 59.8
| WT | HW | 0.07 |  | 100 | 94.6 | 139.5 | 60 | 59.8
| Ent-V. KW | CW | 0.3 |  | 50 | 119.9 | 158.8 | 65.5 | 8.1
| Spüle | HW | 0.07 |  | 100 | 97.7 | 128.5 | 67.9 | 59.7
| Ent-V. KW | CW | 0.3 |  | 50 | 119.9 | 155.4 | 68.9 | 8.1
| Ent-V. KW | CW | 0.3 |  | 50 | 119.9 | 154.1 | 70.2 | 8.1
| Ent-V. KW | CW | 0.3 |  | 50 | 119.9 | 152.7 | 71.5 | 8.1
| H 1 | CW | 1.66 |  | 300 | 11.3 | 11 | 71.8 | 8
| DU | HW | 0.15 |  | 100 | 69.4 | 151.9 | 72.9 | 59.8
| WC | CW | 0.13 |  | 100 | 93.9 | 121 | 79.1 | 8.1
| Spüle | HW | 0.07 |  | 100 | 97.7 | 116.9 | 79.5 | 58.8
| WC | CW | 0.13 |  | 100 | 93.9 | 119.7 | 80.5 | 8.1
| WT | CW | 0.07 |  | 100 | 94.6 | 118.1 | 81.4 | 8.1
| Spüle | CW | 0.07 |  | 100 | 97.7 | 113.9 | 82.5 | 8.1
| WT | CW | 0.07 |  | 100 | 94.6 | 116.5 | 83 | 8.1
| WC | CW | 0.13 |  | 100 | 93.9 | 115.2 | 84.9 | 8.1
| Spüle | CW | 0.07 |  | 100 | 97.7 | 111.2 | 85.3 | 8.2
| WT | HW | 0.07 |  | 100 | 62.6 | 146.1 | 85.5 | 59.7
| H 2 | CW | 1.66 |  | 300 | -4.9 | 12.4 | 86.6 | 8
| WC | CW | 0.13 |  | 100 | 93.9 | 113.4 | 86.8 | 8.1
| WT | CW | 0.07 |  | 100 | 94.6 | 112.1 | 87.4 | 8.1
| Spüle | HW | 0.07 |  | 100 | 97.7 | 108.7 | 87.7 | 59.7
| Spüle | HW | 0.07 |  | 100 | 97.7 | 108.4 | 88 | 59.6
| WT | CW | 0.07 |  | 100 | 94.6 | 110.2 | 89.3 | 8.1
| H 1 | CW | 1.66 |  | 300 | -4.9 | 6.6 | 92.4 | 8
| H 1 | CW | 1.66 |  | 300 | -4.9 | 4.5 | 94.6 | 8
| Spüle | HW | 0.07 |  | 100 | 97.7 | 100.3 | 96.1 | 59.6
| DU | CW | 0.15 |  | 100 | 69.4 | 127.3 | 97.5 | 8.1
| Spüle | CW | 0.07 |  | 100 | 97.7 | 98.7 | 97.7 | 8.1
| Spüle | CW | 0.07 |  | 100 | 97.7 | 92.6 | 103.8 | 8.1
| Spüle | CW | 0.07 |  | 100 | 97.7 | 92.4 | 104 | 8.1
| WT | CW | 0.07 |  | 100 | 62.6 | 121.1 | 110.5 | 8.1
| Spüle | CW | 0.07 |  | 100 | 97.7 | 78.5 | 117.9 | 8.1
| Ent-V. KW | CW | 0.3 |  | 50 | 119.9 | 103.4 | 120.9 | 8.1
| Spüle | HW | 0.07 |  | 100 | 28.3 | 145 | 120.9 | 59.7
| WC | CW | 0.13 |  | 100 | 61.9 | 110.4 | 121.9 | 8
| Ent-V. KW | CW | 0.3 |  | 50 | 119.9 | 100 | 124.3 | 8.1
| WT | HW | 0.07 |  | 100 | 25.2 | 144.4 | 124.6 | 59.8
| WT | HW | 0.07 |  | 100 | 25.2 | 143.3 | 125.6 | 59.8
| Ent-V. KW | CW | 0.3 |  | 50 | 119.9 | 98.2 | 126.1 | 8
| Ent-V. KW | CW | 0.3 |  | 50 | 119.9 | 96.9 | 127.4 | 8
| WT | HW | 0.07 |  | 100 | 9 | 141.8 | 143.3 | 59.7
| WT | HW | 0.07 |  | 100 | 9 | 141.7 | 143.4 | 59.7
| Spüle | CW | 0.07 |  | 100 | 28.3 | 117.8 | 148.1 | 8.1
| WT | CW | 0.07 |  | 100 | 25.2 | 117.2 | 151.7 | 8.1
| WT | CW | 0.07 |  | 100 | 25.2 | 116 | 152.9 | 8
| WC | CW | 0.13 |  | 100 | 24.5 | 114.5 | 155.1 | 8
| WC | CW | 0.13 |  | 100 | 24.5 | 113.8 | 155.8 | 8
| WT | HW | 0.07 |  | 100 | 9 | 127 | 158.1 | 59.8
| WT | HW | 0.07 |  | 100 | 25.2 | 109.6 | 159.3 | 59.9
| Spüle | HW | 0.07 |  | 100 | 28.3 | 105.6 | 160.2 | 59.8
| GS | CW | 0.15 |  | 100 | 24.5 | 104.4 | 165.2 | 8
| Spüle | CW | 0.07 |  | 100 | 28.3 | 100.4 | 165.5 | 8
| WC | CW | 0.13 |  | 100 | 24.5 | 98.1 | 171.5 | 8
| WT | CW | 0.07 |  | 100 | 25.2 | 92.3 | 176.6 | 8
| WC | CW | 0.13 |  | 100 | 8.3 | 99 | 186.8 | 8.1
| WT | CW | 0.07 |  | 100 | 9 | 95.9 | 189.2 | 8
| WT | CW | 0.07 |  | 100 | 9 | 95.8 | 189.3 | 8
| WC | CW | 0.13 |  | 100 | 8.3 | 92.5 | 193.2 | 8
| WC | CW | 0.13 |  | 100 | 8.3 | 92.1 | 193.7 | 8
| Urinal | CW | 0.3 |  | 100 | 11.8 | 85 | 197.3 | 8
| WC | CW | 0.13 |  | 100 | 8.3 | 79.9 | 205.8 | 8
| WT | CW | 0.07 |  | 100 | 9 | 71.7 | 213.4 | 8
| Ent-V. KW | CW | 0.3 |  | 50 | 16.1 | 111.5 | 216.5 | 8
| SV 4 | CW | 0.001 |  | 1 | 2 | 57.4 | 333.7 | 8.4

## Flow paths CW
Flow paths CW
|  | Description |  | Type | L [m] | ΣVr [dm³/s] | Vs [dm³/s] |  | Diam. [mm] |  | Piperun type |  | v [m/s] | R [Pa/m] |  | R*L [kPa] | Σζ | Z [kPa] | Δparm [kPa] | Δp [kPa] | Δθ [K]
Source: no name
Path to receptor: H 4 Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 2 |  | CW | 2.31 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.3 | 4.5 | 1.5 | 0 | 1.8 | 0
|  | 2_a |  | CW | 5.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.8 | 0 | 0 | 0 | 0.8 | 0
|  | 4 |  | CW | 3.38 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.5 | 1.8 | 0.6 | 0 | 1.1 | 0
|  | 4_a |  | CW | 4.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.7 | 1.4 | 0.5 | 0 | 1.2 | 0
|  | 4_b |  | CW | 1.53 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | 6 |  | CW | 4.16 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.6 | 0.4 | 0.1 | 0 | 0.8 | 0
|  | 7 |  | CW | 2.07 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.3 | 1.7 | 0.6 | 0 | 0.9 | 0
|  | 7_a |  | CW | 0.23 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0 | 1.4 | 0.5 | 0 | 0.5 | 0
|  | 7_b |  | CW | 5.22 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.8 | 1.4 | 0.5 | 0 | 1.3 | 0
|  | 7_c |  | CW | 0.24 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 7_d |  | CW | 0.37 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 11 |  | CW | 10.71 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 1.6 | 1.5 | 0.5 | 0 | 2.1 | 0
|  | 12 |  | CW | 0.09 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.32 |  | 0 | 1.7 | 0.6 | 0 | 0.6 | 0
|  | 12_a |  | CW | 3.39 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.32 |  | 0.5 | 2.8 | 0.9 | 0 | 1.4 | 0
|  | 12_b |  | CW | 0.93 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.32 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
ΣΔp = 13,4 kPa
Path to receptor: WC Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 59 |  | CW | 2.21 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.71 |  | 5.2 | 2.4 | 4.7 | 0 | 9.9 | 0
|  | 59_a |  | CW | 0.51 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.69 |  | 1.2 | 2.8 | 5.5 | 0 | 6.7 | 0
|  | 59_b |  | CW | 5.29 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.59 |  | 12.4 | 0 | 0 | 0 | 12.4 | 0
|  | 65 |  | CW | 3.29 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.63 |  | 5.6 | 3.6 | 5 | 0 | 10.6 | 0
|  | 65_a |  | CW | 0.55 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.9 | 0 | 0 | 0 | 0.9 | 0
|  | 65_b |  | CW | 0.05 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 66 |  | CW | 2.1 | 0.87 | 0.501 |  | 25 x 2,5 |  | UNIP_co |  | 1.593 | 1577.09 |  | 3.3 | 3.2 | 4.1 | 0 | 7.4 | 0
|  | 70 |  | CW | 0.9 | 0.67 | 0.43 |  | 25 x 2,5 |  | UNIP_co |  | 1.367 | 1203.91 |  | 1.1 | 0.8 | 0.7 | 0 | 1.8 | 0
|  | 74 |  | CW | 0.91 | 0.47 | 0.346 |  | 20 x 2,25 |  | UNIP_co |  | 1.831 | 2762.2 |  | 2.5 | 0.8 | 1.3 | 0 | 3.8 | 0
|  | 78 |  | CW | 0.35 | 0.27 | 0.238 |  | 18 x 2,0 |  | UNIP_co |  | 1.548 | 2331.51 |  | 0.8 | 2 | 2.4 | 0 | 3.2 | 0
|  | 80 |  | CW | 0.73 | 0.2 | 0.191 |  | 16 x 2,0 |  | UNIP_co |  | 1.685 | 3275.43 |  | 2.4 | 1.4 | 2 | 0 | 4.4 | 0
|  | 81 |  | CW | 0.5 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.56 |  | 0.8 | 5.2 | 3.4 | 0 | 4.3 | 0
ΣΔp = 121,0 kPa
Path to receptor: WT Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 59 |  | CW | 2.21 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.71 |  | 5.2 | 2.4 | 4.7 | 0 | 9.9 | 0
|  | 59_a |  | CW | 0.51 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.69 |  | 1.2 | 2.8 | 5.5 | 0 | 6.7 | 0
|  | 59_b |  | CW | 5.29 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.59 |  | 12.4 | 0 | 0 | 0 | 12.4 | 0
|  | 65 |  | CW | 3.29 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.63 |  | 5.6 | 3.6 | 5 | 0 | 10.6 | 0
|  | 65_a |  | CW | 0.55 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.9 | 0 | 0 | 0 | 0.9 | 0
|  | 65_b |  | CW | 0.05 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 66 |  | CW | 2.1 | 0.87 | 0.501 |  | 25 x 2,5 |  | UNIP_co |  | 1.593 | 1577.09 |  | 3.3 | 3.2 | 4.1 | 0 | 7.4 | 0
|  | 70 |  | CW | 0.9 | 0.67 | 0.43 |  | 25 x 2,5 |  | UNIP_co |  | 1.367 | 1203.91 |  | 1.1 | 0.8 | 0.7 | 0 | 1.8 | 0
|  | 74 |  | CW | 0.91 | 0.47 | 0.346 |  | 20 x 2,25 |  | UNIP_co |  | 1.831 | 2762.2 |  | 2.5 | 0.8 | 1.3 | 0 | 3.8 | 0
|  | 78 |  | CW | 0.35 | 0.27 | 0.238 |  | 18 x 2,0 |  | UNIP_co |  | 1.548 | 2331.51 |  | 0.8 | 2 | 2.4 | 0 | 3.2 | 0
|  | 80 |  | CW | 0.73 | 0.2 | 0.191 |  | 16 x 2,0 |  | UNIP_co |  | 1.685 | 3275.43 |  | 2.4 | 1.4 | 2 | 0 | 4.4 | 0
|  | 82 |  | CW | 1.75 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.64 |  | 1 | 1.6 | 0.3 | 0 | 1.3 | 0
ΣΔp = 118,1 kPa
Path to receptor: WC Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 31 |  | CW | 5.17 | 1.4 | 0.653 |  | 32 x 3,0 |  | UNIP_co |  | 1.231 | 723.36 |  | 3.7 | 0.7 | 0.5 | 0 | 4.3 | 0
|  | 32 |  | CW | 0.16 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.4 | 2.6 | 5 | 0 | 5.4 | 0
|  | 32_a |  | CW | 0.32 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.7 | 2.8 | 5.4 | 0 | 6.1 | 0
|  | 32_b |  | CW | 1.45 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.8 |  | 3.3 | 0 | 0 | 0 | 3.3 | 0
|  | 33 |  | CW | 0.31 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.62 |  | 0.7 | 3.2 | 5.8 | 0 | 6.4 | 0
|  | 33_a |  | CW | 0.32 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.61 |  | 0.7 | 1.6 | 2.9 | 0.1 | 3.7 | 0
|  | 34 |  | CW | 0.32 | 0.97 | 0.533 |  | 25 x 2,5 |  | UNIP_co |  | 1.696 | 1760.59 |  | 0.6 | 3.2 | 4.6 | 0 | 5.2 | 0
|  | 35 |  | CW | 7.62 | 0.77 | 0.466 |  | 25 x 2,5 |  | UNIP_co |  | 1.484 | 1391.88 |  | 10.6 | 4 | 4.4 | 0 | 15 | 0
|  | 37 |  | CW | 1.31 | 0.47 | 0.346 |  | 20 x 2,25 |  | UNIP_co |  | 1.831 | 2762.49 |  | 3.6 | 0.8 | 1.3 | 0 | 5 | 0
|  | 42 |  | CW | 1.31 | 0.26 | 0.232 |  | 18 x 2,0 |  | UNIP_co |  | 1.507 | 2223.19 |  | 2.9 | 2.4 | 2.7 | 0 | 5.6 | 0
|  | 43 |  | CW | 0.49 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.73 |  | 0.8 | 4.2 | 2.8 | 0 | 3.6 | 0
ΣΔp = 114,5 kPa
Path to receptor: WC Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 59 |  | CW | 2.21 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.71 |  | 5.2 | 2.4 | 4.7 | 0 | 9.9 | 0
|  | 59_a |  | CW | 0.51 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.69 |  | 1.2 | 2.8 | 5.5 | 0 | 6.7 | 0
|  | 59_b |  | CW | 5.29 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.59 |  | 12.4 | 0 | 0 | 0 | 12.4 | 0
|  | 65 |  | CW | 3.29 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.63 |  | 5.6 | 3.6 | 5 | 0 | 10.6 | 0
|  | 65_a |  | CW | 0.55 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.9 | 0 | 0 | 0 | 0.9 | 0
|  | 65_b |  | CW | 0.05 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 66 |  | CW | 2.1 | 0.87 | 0.501 |  | 25 x 2,5 |  | UNIP_co |  | 1.593 | 1577.09 |  | 3.3 | 3.2 | 4.1 | 0 | 7.4 | 0
|  | 70 |  | CW | 0.9 | 0.67 | 0.43 |  | 25 x 2,5 |  | UNIP_co |  | 1.367 | 1203.91 |  | 1.1 | 0.8 | 0.7 | 0 | 1.8 | 0
|  | 74 |  | CW | 0.91 | 0.47 | 0.346 |  | 20 x 2,25 |  | UNIP_co |  | 1.831 | 2762.2 |  | 2.5 | 0.8 | 1.3 | 0 | 3.8 | 0
|  | 75 |  | CW | 0.28 | 0.2 | 0.191 |  | 16 x 2,0 |  | UNIP_co |  | 1.685 | 3275.47 |  | 0.9 | 3.6 | 5.1 | 0 | 6 | 0
|  | 76 |  | CW | 0.6 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.59 |  | 1 | 5.2 | 3.4 | 0 | 4.4 | 0
ΣΔp = 119,7 kPa
Path to receptor: WT Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 31 |  | CW | 5.17 | 1.4 | 0.653 |  | 32 x 3,0 |  | UNIP_co |  | 1.231 | 723.36 |  | 3.7 | 0.7 | 0.5 | 0 | 4.3 | 0
|  | 32 |  | CW | 0.16 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.4 | 2.6 | 5 | 0 | 5.4 | 0
|  | 32_a |  | CW | 0.32 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.7 | 2.8 | 5.4 | 0 | 6.1 | 0
|  | 32_b |  | CW | 1.45 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.8 |  | 3.3 | 0 | 0 | 0 | 3.3 | 0
|  | 33 |  | CW | 0.31 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.62 |  | 0.7 | 3.2 | 5.8 | 0 | 6.4 | 0
|  | 33_a |  | CW | 0.32 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.61 |  | 0.7 | 1.6 | 2.9 | 0.1 | 3.7 | 0
|  | 34 |  | CW | 0.32 | 0.97 | 0.533 |  | 25 x 2,5 |  | UNIP_co |  | 1.696 | 1760.59 |  | 0.6 | 3.2 | 4.6 | 0 | 5.2 | 0
|  | 35 |  | CW | 7.62 | 0.77 | 0.466 |  | 25 x 2,5 |  | UNIP_co |  | 1.484 | 1391.88 |  | 10.6 | 4 | 4.4 | 0 | 15 | 0
|  | 37 |  | CW | 1.31 | 0.47 | 0.346 |  | 20 x 2,25 |  | UNIP_co |  | 1.831 | 2762.49 |  | 3.6 | 0.8 | 1.3 | 0 | 5 | 0
|  | 38 |  | CW | 1.24 | 0.21 | 0.198 |  | 16 x 2,0 |  | UNIP_co |  | 1.75 | 3500.85 |  | 4.3 | 3.6 | 5.5 | 0 | 9.8 | 0
|  | 39 |  | CW | 1.36 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.71 |  | 0.8 | 6.8 | 1.3 | 0 | 2.1 | 0
ΣΔp = 117,2 kPa
Path to receptor: H 3 Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 2 |  | CW | 2.31 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.3 | 4.5 | 1.5 | 0 | 1.8 | 0
|  | 2_a |  | CW | 5.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.8 | 0 | 0 | 0 | 0.8 | 0
|  | 4 |  | CW | 3.38 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.5 | 1.8 | 0.6 | 0 | 1.1 | 0
|  | 4_a |  | CW | 4.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.7 | 1.4 | 0.5 | 0 | 1.2 | 0
|  | 4_b |  | CW | 1.53 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | 6 |  | CW | 4.16 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.6 | 0.4 | 0.1 | 0 | 0.8 | 0
|  | 7 |  | CW | 2.07 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.3 | 1.7 | 0.6 | 0 | 0.9 | 0
|  | 7_a |  | CW | 0.23 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0 | 1.4 | 0.5 | 0 | 0.5 | 0
|  | 7_b |  | CW | 5.22 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.8 | 1.4 | 0.5 | 0 | 1.3 | 0
|  | 7_c |  | CW | 0.24 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 7_d |  | CW | 0.37 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 8 |  | CW | 1.98 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.3 | 1.5 | 0.5 | 0 | 0.8 | 0
|  | 10 |  | CW | 1.02 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.2 | 1.8 | 0.6 | 0 | 0.7 | 0
|  | 10_a |  | CW | 3.25 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.5 | 2.8 | 0.9 | 0 | 1.4 | 0
|  | 10_b |  | CW | 1.01 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.32 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
ΣΔp = 12,3 kPa
Path to receptor: WC Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 31 |  | CW | 5.17 | 1.4 | 0.653 |  | 32 x 3,0 |  | UNIP_co |  | 1.231 | 723.36 |  | 3.7 | 0.7 | 0.5 | 0 | 4.3 | 0
|  | 32 |  | CW | 0.16 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.4 | 2.6 | 5 | 0 | 5.4 | 0
|  | 32_a |  | CW | 0.32 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.7 | 2.8 | 5.4 | 0 | 6.1 | 0
|  | 32_b |  | CW | 1.45 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.8 |  | 3.3 | 0 | 0 | 0 | 3.3 | 0
|  | 33 |  | CW | 0.31 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.62 |  | 0.7 | 3.2 | 5.8 | 0 | 6.4 | 0
|  | 33_a |  | CW | 0.32 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.61 |  | 0.7 | 1.6 | 2.9 | 0.1 | 3.7 | 0
|  | 34 |  | CW | 0.32 | 0.97 | 0.533 |  | 25 x 2,5 |  | UNIP_co |  | 1.696 | 1760.59 |  | 0.6 | 3.2 | 4.6 | 0 | 5.2 | 0
|  | 35 |  | CW | 7.62 | 0.77 | 0.466 |  | 25 x 2,5 |  | UNIP_co |  | 1.484 | 1391.88 |  | 10.6 | 4 | 4.4 | 0 | 15 | 0
|  | 37 |  | CW | 1.31 | 0.47 | 0.346 |  | 20 x 2,25 |  | UNIP_co |  | 1.831 | 2762.49 |  | 3.6 | 0.8 | 1.3 | 0 | 5 | 0
|  | 42 |  | CW | 1.31 | 0.26 | 0.232 |  | 18 x 2,0 |  | UNIP_co |  | 1.507 | 2223.19 |  | 2.9 | 2.4 | 2.7 | 0 | 5.6 | 0
|  | 44 |  | CW | 1.18 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.71 |  | 2 | 1.4 | 0.9 | 0 | 2.9 | 0
ΣΔp = 113,8 kPa
Path to receptor: WT Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 31 |  | CW | 5.17 | 1.4 | 0.653 |  | 32 x 3,0 |  | UNIP_co |  | 1.231 | 723.36 |  | 3.7 | 0.7 | 0.5 | 0 | 4.3 | 0
|  | 32 |  | CW | 0.16 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.4 | 2.6 | 5 | 0 | 5.4 | 0
|  | 32_a |  | CW | 0.32 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.7 | 2.8 | 5.4 | 0 | 6.1 | 0
|  | 32_b |  | CW | 1.45 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.8 |  | 3.3 | 0 | 0 | 0 | 3.3 | 0
|  | 33 |  | CW | 0.31 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.62 |  | 0.7 | 3.2 | 5.8 | 0 | 6.4 | 0
|  | 33_a |  | CW | 0.32 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.61 |  | 0.7 | 1.6 | 2.9 | 0.1 | 3.7 | 0
|  | 34 |  | CW | 0.32 | 0.97 | 0.533 |  | 25 x 2,5 |  | UNIP_co |  | 1.696 | 1760.59 |  | 0.6 | 3.2 | 4.6 | 0 | 5.2 | 0
|  | 35 |  | CW | 7.62 | 0.77 | 0.466 |  | 25 x 2,5 |  | UNIP_co |  | 1.484 | 1391.88 |  | 10.6 | 4 | 4.4 | 0 | 15 | 0
|  | 37 |  | CW | 1.31 | 0.47 | 0.346 |  | 20 x 2,25 |  | UNIP_co |  | 1.831 | 2762.49 |  | 3.6 | 0.8 | 1.3 | 0 | 5 | 0
|  | 38 |  | CW | 1.24 | 0.21 | 0.198 |  | 16 x 2,0 |  | UNIP_co |  | 1.75 | 3500.85 |  | 4.3 | 3.6 | 5.5 | 0 | 9.8 | 0
|  | 40 |  | CW | 0.78 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.72 |  | 0.4 | 2.4 | 0.5 | 0 | 0.9 | 0
ΣΔp = 116,0 kPa
Path to receptor: WT Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 59 |  | CW | 2.21 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.71 |  | 5.2 | 2.4 | 4.7 | 0 | 9.9 | 0
|  | 59_a |  | CW | 0.51 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.69 |  | 1.2 | 2.8 | 5.5 | 0 | 6.7 | 0
|  | 59_b |  | CW | 5.29 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.59 |  | 12.4 | 0 | 0 | 0 | 12.4 | 0
|  | 65 |  | CW | 3.29 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.63 |  | 5.6 | 3.6 | 5 | 0 | 10.6 | 0
|  | 65_a |  | CW | 0.55 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.9 | 0 | 0 | 0 | 0.9 | 0
|  | 65_b |  | CW | 0.05 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 66 |  | CW | 2.1 | 0.87 | 0.501 |  | 25 x 2,5 |  | UNIP_co |  | 1.593 | 1577.09 |  | 3.3 | 3.2 | 4.1 | 0 | 7.4 | 0
|  | 70 |  | CW | 0.9 | 0.67 | 0.43 |  | 25 x 2,5 |  | UNIP_co |  | 1.367 | 1203.91 |  | 1.1 | 0.8 | 0.7 | 0 | 1.8 | 0
|  | 74 |  | CW | 0.91 | 0.47 | 0.346 |  | 20 x 2,25 |  | UNIP_co |  | 1.831 | 2762.2 |  | 2.5 | 0.8 | 1.3 | 0 | 3.8 | 0
|  | 75 |  | CW | 0.28 | 0.2 | 0.191 |  | 16 x 2,0 |  | UNIP_co |  | 1.685 | 3275.47 |  | 0.9 | 3.6 | 5.1 | 0 | 6 | 0
|  | 77 |  | CW | 1.64 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.66 |  | 0.9 | 1.6 | 0.3 | 0 | 1.2 | 0
ΣΔp = 116,5 kPa
Path to receptor: Spüle Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 31 |  | CW | 5.17 | 1.4 | 0.653 |  | 32 x 3,0 |  | UNIP_co |  | 1.231 | 723.36 |  | 3.7 | 0.7 | 0.5 | 0 | 4.3 | 0
|  | 32 |  | CW | 0.16 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.4 | 2.6 | 5 | 0 | 5.4 | 0
|  | 32_a |  | CW | 0.32 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.7 | 2.8 | 5.4 | 0 | 6.1 | 0
|  | 32_b |  | CW | 1.45 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.8 |  | 3.3 | 0 | 0 | 0 | 3.3 | 0
|  | 33 |  | CW | 0.31 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.62 |  | 0.7 | 3.2 | 5.8 | 0 | 6.4 | 0
|  | 33_a |  | CW | 0.32 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.61 |  | 0.7 | 1.6 | 2.9 | 0.1 | 3.7 | 0
|  | 34 |  | CW | 0.32 | 0.97 | 0.533 |  | 25 x 2,5 |  | UNIP_co |  | 1.696 | 1760.59 |  | 0.6 | 3.2 | 4.6 | 0 | 5.2 | 0
|  | 35 |  | CW | 7.62 | 0.77 | 0.466 |  | 25 x 2,5 |  | UNIP_co |  | 1.484 | 1391.88 |  | 10.6 | 4 | 4.4 | 0 | 15 | 0
|  | 37 |  | CW | 1.31 | 0.47 | 0.346 |  | 20 x 2,25 |  | UNIP_co |  | 1.831 | 2762.49 |  | 3.6 | 0.8 | 1.3 | 0 | 5 | 0
|  | 38 |  | CW | 1.24 | 0.21 | 0.198 |  | 16 x 2,0 |  | UNIP_co |  | 1.75 | 3500.85 |  | 4.3 | 3.6 | 5.5 | 0 | 9.8 | 0
|  | 41 |  | CW | 2.63 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.69 |  | 1.5 | 6 | 1.1 | 0 | 2.6 | 0
ΣΔp = 117,8 kPa
Path to receptor: Spüle Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 59 |  | CW | 2.21 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.71 |  | 5.2 | 2.4 | 4.7 | 0 | 9.9 | 0
|  | 59_a |  | CW | 0.51 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.69 |  | 1.2 | 2.8 | 5.5 | 0 | 6.7 | 0
|  | 59_b |  | CW | 5.29 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.59 |  | 12.4 | 0 | 0 | 0 | 12.4 | 0
|  | 65 |  | CW | 3.29 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.63 |  | 5.6 | 3.6 | 5 | 0 | 10.6 | 0
|  | 65_a |  | CW | 0.55 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.9 | 0 | 0 | 0 | 0.9 | 0
|  | 65_b |  | CW | 0.05 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 66 |  | CW | 2.1 | 0.87 | 0.501 |  | 25 x 2,5 |  | UNIP_co |  | 1.593 | 1577.09 |  | 3.3 | 3.2 | 4.1 | 0 | 7.4 | 0
|  | 70 |  | CW | 0.9 | 0.67 | 0.43 |  | 25 x 2,5 |  | UNIP_co |  | 1.367 | 1203.91 |  | 1.1 | 0.8 | 0.7 | 0 | 1.8 | 0
|  | 74 |  | CW | 0.91 | 0.47 | 0.346 |  | 20 x 2,25 |  | UNIP_co |  | 1.831 | 2762.2 |  | 2.5 | 0.8 | 1.3 | 0 | 3.8 | 0
|  | 78 |  | CW | 0.35 | 0.27 | 0.238 |  | 18 x 2,0 |  | UNIP_co |  | 1.548 | 2331.51 |  | 0.8 | 2 | 2.4 | 0 | 3.2 | 0
|  | 79 |  | CW | 1.22 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.66 |  | 0.7 | 4.2 | 0.8 | 0 | 1.5 | 0
ΣΔp = 113,9 kPa
Path to receptor: WC Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 59 |  | CW | 2.21 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.71 |  | 5.2 | 2.4 | 4.7 | 0 | 9.9 | 0
|  | 59_a |  | CW | 0.51 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.69 |  | 1.2 | 2.8 | 5.5 | 0 | 6.7 | 0
|  | 59_b |  | CW | 5.29 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.59 |  | 12.4 | 0 | 0 | 0 | 12.4 | 0
|  | 65 |  | CW | 3.29 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.63 |  | 5.6 | 3.6 | 5 | 0 | 10.6 | 0
|  | 65_a |  | CW | 0.55 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.9 | 0 | 0 | 0 | 0.9 | 0
|  | 65_b |  | CW | 0.05 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 66 |  | CW | 2.1 | 0.87 | 0.501 |  | 25 x 2,5 |  | UNIP_co |  | 1.593 | 1577.09 |  | 3.3 | 3.2 | 4.1 | 0 | 7.4 | 0
|  | 70 |  | CW | 0.9 | 0.67 | 0.43 |  | 25 x 2,5 |  | UNIP_co |  | 1.367 | 1203.91 |  | 1.1 | 0.8 | 0.7 | 0 | 1.8 | 0
|  | 71 |  | CW | 0.28 | 0.2 | 0.191 |  | 16 x 2,0 |  | UNIP_co |  | 1.685 | 3275.51 |  | 0.9 | 3.2 | 4.5 | 0 | 5.5 | 0
|  | 72 |  | CW | 0.59 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.61 |  | 1 | 5.2 | 3.4 | 0 | 4.4 | 0
ΣΔp = 115,2 kPa
Path to receptor: WC Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 31 |  | CW | 5.17 | 1.4 | 0.653 |  | 32 x 3,0 |  | UNIP_co |  | 1.231 | 723.36 |  | 3.7 | 0.7 | 0.5 | 0 | 4.3 | 0
|  | 32 |  | CW | 0.16 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.4 | 2.6 | 5 | 0 | 5.4 | 0
|  | 32_a |  | CW | 0.32 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.7 | 2.8 | 5.4 | 0 | 6.1 | 0
|  | 32_b |  | CW | 1.45 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.8 |  | 3.3 | 0 | 0 | 0 | 3.3 | 0
|  | 33 |  | CW | 0.31 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.62 |  | 0.7 | 3.2 | 5.8 | 0 | 6.4 | 0
|  | 33_a |  | CW | 0.32 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.61 |  | 0.7 | 1.6 | 2.9 | 0.1 | 3.7 | 0
|  | 34 |  | CW | 0.32 | 0.97 | 0.533 |  | 25 x 2,5 |  | UNIP_co |  | 1.696 | 1760.59 |  | 0.6 | 3.2 | 4.6 | 0 | 5.2 | 0
|  | 45 |  | CW | 0.77 | 0.2 | 0.191 |  | 16 x 2,0 |  | UNIP_co |  | 1.685 | 3276.17 |  | 2.5 | 2.2 | 3.1 | 0 | 5.6 | 0
|  | 47 |  | CW | 1.58 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.91 |  | 2.6 | 5.6 | 3.7 | 0 | 6.3 | 0
|  | 47_a |  | CW | 0.49 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.85 |  | 0.8 | 0 | 0 | 0 | 0.8 | 0
ΣΔp = 98,1 kPa
Path to receptor: WT Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 59 |  | CW | 2.21 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.71 |  | 5.2 | 2.4 | 4.7 | 0 | 9.9 | 0
|  | 59_a |  | CW | 0.51 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.69 |  | 1.2 | 2.8 | 5.5 | 0 | 6.7 | 0
|  | 59_b |  | CW | 5.29 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.59 |  | 12.4 | 0 | 0 | 0 | 12.4 | 0
|  | 65 |  | CW | 3.29 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.63 |  | 5.6 | 3.6 | 5 | 0 | 10.6 | 0
|  | 65_a |  | CW | 0.55 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.9 | 0 | 0 | 0 | 0.9 | 0
|  | 65_b |  | CW | 0.05 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 66 |  | CW | 2.1 | 0.87 | 0.501 |  | 25 x 2,5 |  | UNIP_co |  | 1.593 | 1577.09 |  | 3.3 | 3.2 | 4.1 | 0 | 7.4 | 0
|  | 70 |  | CW | 0.9 | 0.67 | 0.43 |  | 25 x 2,5 |  | UNIP_co |  | 1.367 | 1203.91 |  | 1.1 | 0.8 | 0.7 | 0 | 1.8 | 0
|  | 71 |  | CW | 0.28 | 0.2 | 0.191 |  | 16 x 2,0 |  | UNIP_co |  | 1.685 | 3275.51 |  | 0.9 | 3.2 | 4.5 | 0 | 5.5 | 0
|  | 73 |  | CW | 1.65 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.66 |  | 0.9 | 1.6 | 0.3 | 0 | 1.2 | 0
ΣΔp = 112,1 kPa
Path to receptor: WT Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 59 |  | CW | 2.21 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.71 |  | 5.2 | 2.4 | 4.7 | 0 | 9.9 | 0
|  | 59_a |  | CW | 0.51 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.69 |  | 1.2 | 2.8 | 5.5 | 0 | 6.7 | 0
|  | 59_b |  | CW | 5.29 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.59 |  | 12.4 | 0 | 0 | 0 | 12.4 | 0
|  | 65 |  | CW | 3.29 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.63 |  | 5.6 | 3.6 | 5 | 0 | 10.6 | 0
|  | 65_a |  | CW | 0.55 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.9 | 0 | 0 | 0 | 0.9 | 0
|  | 65_b |  | CW | 0.05 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 66 |  | CW | 2.1 | 0.87 | 0.501 |  | 25 x 2,5 |  | UNIP_co |  | 1.593 | 1577.09 |  | 3.3 | 3.2 | 4.1 | 0 | 7.4 | 0
|  | 67 |  | CW | 0.28 | 0.2 | 0.191 |  | 16 x 2,0 |  | UNIP_co |  | 1.685 | 3275.55 |  | 0.9 | 3.2 | 4.5 | 0 | 5.5 | 0
|  | 69 |  | CW | 1.65 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.67 |  | 0.9 | 1.6 | 0.3 | 0 | 1.2 | 0
ΣΔp = 110,2 kPa
Path to receptor: WT Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 31 |  | CW | 5.17 | 1.4 | 0.653 |  | 32 x 3,0 |  | UNIP_co |  | 1.231 | 723.36 |  | 3.7 | 0.7 | 0.5 | 0 | 4.3 | 0
|  | 32 |  | CW | 0.16 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.4 | 2.6 | 5 | 0 | 5.4 | 0
|  | 32_a |  | CW | 0.32 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.7 | 2.8 | 5.4 | 0 | 6.1 | 0
|  | 32_b |  | CW | 1.45 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.8 |  | 3.3 | 0 | 0 | 0 | 3.3 | 0
|  | 33 |  | CW | 0.31 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.62 |  | 0.7 | 3.2 | 5.8 | 0 | 6.4 | 0
|  | 33_a |  | CW | 0.32 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.61 |  | 0.7 | 1.6 | 2.9 | 0.1 | 3.7 | 0
|  | 34 |  | CW | 0.32 | 0.97 | 0.533 |  | 25 x 2,5 |  | UNIP_co |  | 1.696 | 1760.59 |  | 0.6 | 3.2 | 4.6 | 0 | 5.2 | 0
|  | 45 |  | CW | 0.77 | 0.2 | 0.191 |  | 16 x 2,0 |  | UNIP_co |  | 1.685 | 3276.17 |  | 2.5 | 2.2 | 3.1 | 0 | 5.6 | 0
|  | 46 |  | CW | 0.61 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.8 |  | 0.3 | 5.2 | 1 | 0 | 1.3 | 0
ΣΔp = 92,3 kPa
Path to receptor: H 3 Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 2 |  | CW | 2.31 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.3 | 4.5 | 1.5 | 0 | 1.8 | 0
|  | 2_a |  | CW | 5.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.8 | 0 | 0 | 0 | 0.8 | 0
|  | 4 |  | CW | 3.38 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.5 | 1.8 | 0.6 | 0 | 1.1 | 0
|  | 4_a |  | CW | 4.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.7 | 1.4 | 0.5 | 0 | 1.2 | 0
|  | 4_b |  | CW | 1.53 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | 6 |  | CW | 4.16 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.6 | 0.4 | 0.1 | 0 | 0.8 | 0
|  | 14 |  | CW | 12.11 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 1.8 | 0.4 | 0.1 | 0 | 2 | 0
|  | 15 |  | CW | 4.04 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.6 | 1.7 | 0.6 | 0 | 1.2 | 0
|  | 15_a |  | CW | 0.2 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0 | 1.4 | 0.5 | 0 | 0.5 | 0
|  | 15_b |  | CW | 1.42 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | 17 |  | CW | 3.78 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.6 | 0.4 | 0.1 | 0 | 0.7 | 0
|  | 19 |  | CW | 3.28 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.32 |  | 0.5 | 1.8 | 0.6 | 0 | 1.1 | 0
|  | 19_a |  | CW | 1.13 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.32 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
ΣΔp = 12,3 kPa
Path to receptor: H 2 Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 2 |  | CW | 2.31 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.3 | 4.5 | 1.5 | 0 | 1.8 | 0
|  | 2_a |  | CW | 5.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.8 | 0 | 0 | 0 | 0.8 | 0
|  | 4 |  | CW | 3.38 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.5 | 1.8 | 0.6 | 0 | 1.1 | 0
|  | 4_a |  | CW | 4.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.7 | 1.4 | 0.5 | 0 | 1.2 | 0
|  | 4_b |  | CW | 1.53 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | 6 |  | CW | 4.16 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.6 | 0.4 | 0.1 | 0 | 0.8 | 0
|  | 14 |  | CW | 12.11 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 1.8 | 0.4 | 0.1 | 0 | 2 | 0
|  | 15 |  | CW | 4.04 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.6 | 1.7 | 0.6 | 0 | 1.2 | 0
|  | 15_a |  | CW | 0.2 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0 | 1.4 | 0.5 | 0 | 0.5 | 0
|  | 15_b |  | CW | 1.42 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | 17 |  | CW | 3.78 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.6 | 0.4 | 0.1 | 0 | 0.7 | 0
|  | 18 |  | CW | 0.28 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.32 |  | 0 | 1.7 | 0.6 | 0 | 0.6 | 0
|  | 18_a |  | CW | 1.11 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.32 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
ΣΔp = 11,8 kPa
Path to receptor: Ent-V. KW Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 31 |  | CW | 5.17 | 1.4 | 0.653 |  | 32 x 3,0 |  | UNIP_co |  | 1.231 | 723.36 |  | 3.7 | 0.7 | 0.5 | 0 | 4.3 | 0
|  | 32 |  | CW | 0.16 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.4 | 2.6 | 5 | 0 | 5.4 | 0
|  | 32_a |  | CW | 0.32 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.7 | 2.8 | 5.4 | 0 | 6.1 | 0
|  | 32_b |  | CW | 1.45 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.8 |  | 3.3 | 0 | 0 | 0 | 3.3 | 0
|  | 33 |  | CW | 0.31 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.62 |  | 0.7 | 3.2 | 5.8 | 0 | 6.4 | 0
|  | 33_a |  | CW | 0.32 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.61 |  | 0.7 | 1.6 | 2.9 | 0.1 | 3.7 | 0
|  | 34 |  | CW | 0.32 | 0.97 | 0.533 |  | 25 x 2,5 |  | UNIP_co |  | 1.696 | 1760.59 |  | 0.6 | 3.2 | 4.6 | 0 | 5.2 | 0
|  | 35 |  | CW | 7.62 | 0.77 | 0.466 |  | 25 x 2,5 |  | UNIP_co |  | 1.484 | 1391.88 |  | 10.6 | 4 | 4.4 | 0 | 15 | 0
|  | 36 |  | CW | 0.81 | 0.3 | 0.3 |  | 18 x 2,0 |  | UNIP_co |  | 1.949 | 3496.44 |  | 2.8 | 4.4 | 8.4 | 0 | 11.2 | 0
ΣΔp = 111,5 kPa
Path to receptor: H 1 Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 2 |  | CW | 2.31 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.3 | 4.5 | 1.5 | 0 | 1.8 | 0
|  | 2_a |  | CW | 5.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.8 | 0 | 0 | 0 | 0.8 | 0
|  | 4 |  | CW | 3.38 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.5 | 1.8 | 0.6 | 0 | 1.1 | 0
|  | 4_a |  | CW | 4.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.7 | 1.4 | 0.5 | 0 | 1.2 | 0
|  | 4_b |  | CW | 1.53 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | 6 |  | CW | 4.16 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.6 | 0.4 | 0.1 | 0 | 0.8 | 0
|  | 7 |  | CW | 2.07 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.3 | 1.7 | 0.6 | 0 | 0.9 | 0
|  | 7_a |  | CW | 0.23 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0 | 1.4 | 0.5 | 0 | 0.5 | 0
|  | 7_b |  | CW | 5.22 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.8 | 1.4 | 0.5 | 0 | 1.3 | 0
|  | 7_c |  | CW | 0.24 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 7_d |  | CW | 0.37 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 8 |  | CW | 1.98 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.3 | 1.5 | 0.5 | 0 | 0.8 | 0
|  | 9 |  | CW | 1.39 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.2 | 1.7 | 0.6 | 0 | 0.8 | 0
ΣΔp = 10,7 kPa
Path to receptor: WC Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 59 |  | CW | 2.21 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.71 |  | 5.2 | 2.4 | 4.7 | 0 | 9.9 | 0
|  | 59_a |  | CW | 0.51 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.69 |  | 1.2 | 2.8 | 5.5 | 0 | 6.7 | 0
|  | 59_b |  | CW | 5.29 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.59 |  | 12.4 | 0 | 0 | 0 | 12.4 | 0
|  | 65 |  | CW | 3.29 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.63 |  | 5.6 | 3.6 | 5 | 0 | 10.6 | 0
|  | 65_a |  | CW | 0.55 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.9 | 0 | 0 | 0 | 0.9 | 0
|  | 65_b |  | CW | 0.05 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 66 |  | CW | 2.1 | 0.87 | 0.501 |  | 25 x 2,5 |  | UNIP_co |  | 1.593 | 1577.09 |  | 3.3 | 3.2 | 4.1 | 0 | 7.4 | 0
|  | 67 |  | CW | 0.28 | 0.2 | 0.191 |  | 16 x 2,0 |  | UNIP_co |  | 1.685 | 3275.55 |  | 0.9 | 3.2 | 4.5 | 0 | 5.5 | 0
|  | 68 |  | CW | 0.59 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.63 |  | 1 | 5.2 | 3.4 | 0 | 4.4 | 0
ΣΔp = 113,4 kPa
Path to receptor: H 2 Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 2 |  | CW | 2.31 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.3 | 4.5 | 1.5 | 0 | 1.8 | 0
|  | 2_a |  | CW | 5.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.8 | 0 | 0 | 0 | 0.8 | 0
|  | 4 |  | CW | 3.38 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.5 | 1.8 | 0.6 | 0 | 1.1 | 0
|  | 4_a |  | CW | 4.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.7 | 1.4 | 0.5 | 0 | 1.2 | 0
|  | 4_b |  | CW | 1.53 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | 6 |  | CW | 4.16 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.6 | 0.4 | 0.1 | 0 | 0.8 | 0
|  | 7 |  | CW | 2.07 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.3 | 1.7 | 0.6 | 0 | 0.9 | 0
|  | 7_a |  | CW | 0.23 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0 | 1.4 | 0.5 | 0 | 0.5 | 0
|  | 7_b |  | CW | 5.22 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.8 | 1.4 | 0.5 | 0 | 1.3 | 0
|  | 7_c |  | CW | 0.24 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 7_d |  | CW | 0.37 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 11 |  | CW | 10.71 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 1.6 | 1.5 | 0.5 | 0 | 2.1 | 0
|  | 13 |  | CW | 4.25 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.32 |  | 0.6 | 1.8 | 0.6 | 0 | 1.2 | 0
ΣΔp = 12,5 kPa
Path to receptor: Ent-V. KW Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 84 |  | CW | 1.83 | 2.3 | 0.852 |  | 32 x 3,0 |  | UNIP_co |  | 1.605 | 1156.2 |  | 2.1 | 0.5 | 0.6 | 0 | 2.8 | 0
|  | 100 |  | CW | 15.94 | 1.27 | 0.619 |  | 25 x 2,5 |  | UNIP_co |  | 1.972 | 2298.32 |  | 36.6 | 0.7 | 1.4 | 0 | 38 | 0
|  | 102 |  | CW | 5.5 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.18 |  | 12 | 1.2 | 2.2 | 0 | 14.1 | 0
|  | 102_a |  | CW | 11.26 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2173.93 |  | 24.5 | 0.8 | 1.5 | 0 | 25.9 | 0
|  | 102_b |  | CW | 3.58 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2173.68 |  | 7.8 | 0.4 | 0.7 | 0 | 8.5 | 0
|  | 104 |  | CW | 0.17 | 0.9 | 0.51 |  | 25 x 2,5 |  | UNIP_co |  | 1.625 | 1631.99 |  | 0.3 | 0.8 | 1.1 | 0 | 1.3 | 0
|  | 106 |  | CW | 3.6 | 0.6 | 0.402 |  | 25 x 2,5 |  | UNIP_co |  | 1.279 | 1070.78 |  | 3.9 | 0.8 | 0.7 | 0 | 4.5 | 0
|  | 107 |  | CW | 0.55 | 0.3 | 0.3 |  | 18 x 2,0 |  | UNIP_co |  | 1.949 | 3495.36 |  | 1.9 | 3.2 | 6.1 | 0 | 8 | 0
ΣΔp = 158,8 kPa
Path to receptor: WC Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 84 |  | CW | 1.83 | 2.3 | 0.852 |  | 32 x 3,0 |  | UNIP_co |  | 1.605 | 1156.2 |  | 2.1 | 0.5 | 0.6 | 0 | 2.8 | 0
|  | 85 |  | CW | 4.43 | 1.03 | 0.551 |  | 25 x 2,5 |  | UNIP_co |  | 1.754 | 1869.48 |  | 8.3 | 2.6 | 4 | 0 | 12.3 | 0
|  | 87 |  | CW | 1.96 | 0.96 | 0.53 |  | 25 x 2,5 |  | UNIP_co |  | 1.686 | 1742.27 |  | 3.4 | 0.8 | 1.1 | 0 | 4.5 | 0
|  | 89 |  | CW | 0.78 | 0.66 | 0.426 |  | 25 x 2,5 |  | UNIP_co |  | 1.355 | 1185.14 |  | 0.9 | 0.8 | 0.7 | 0 | 1.7 | 0
|  | 91 |  | CW | 1.53 | 0.53 | 0.373 |  | 20 x 2,25 |  | UNIP_co |  | 1.974 | 3154.21 |  | 4.8 | 1.2 | 2.3 | 0 | 7.2 | 0
|  | 95 |  | CW | 2.49 | 0.27 | 0.238 |  | 18 x 2,0 |  | UNIP_co |  | 1.548 | 2331.74 |  | 5.8 | 0.8 | 1 | 0 | 6.8 | 0
|  | 99 |  | CW | 2.24 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.67 |  | 3.8 | 5.4 | 3.6 | 0 | 7.3 | 0
|  | 99_a |  | CW | 0.55 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.59 |  | 0.9 | 0 | 0 | 0 | 0.9 | 0
ΣΔp = 99,0 kPa
Path to receptor: WT Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 84 |  | CW | 1.83 | 2.3 | 0.852 |  | 32 x 3,0 |  | UNIP_co |  | 1.605 | 1156.2 |  | 2.1 | 0.5 | 0.6 | 0 | 2.8 | 0
|  | 85 |  | CW | 4.43 | 1.03 | 0.551 |  | 25 x 2,5 |  | UNIP_co |  | 1.754 | 1869.48 |  | 8.3 | 2.6 | 4 | 0 | 12.3 | 0
|  | 87 |  | CW | 1.96 | 0.96 | 0.53 |  | 25 x 2,5 |  | UNIP_co |  | 1.686 | 1742.27 |  | 3.4 | 0.8 | 1.1 | 0 | 4.5 | 0
|  | 89 |  | CW | 0.78 | 0.66 | 0.426 |  | 25 x 2,5 |  | UNIP_co |  | 1.355 | 1185.14 |  | 0.9 | 0.8 | 0.7 | 0 | 1.7 | 0
|  | 91 |  | CW | 1.53 | 0.53 | 0.373 |  | 20 x 2,25 |  | UNIP_co |  | 1.974 | 3154.21 |  | 4.8 | 1.2 | 2.3 | 0 | 7.2 | 0
|  | 95 |  | CW | 2.49 | 0.27 | 0.238 |  | 18 x 2,0 |  | UNIP_co |  | 1.548 | 2331.74 |  | 5.8 | 0.8 | 1 | 0 | 6.8 | 0
|  | 96 |  | CW | 0.28 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1942.99 |  | 0.5 | 4.2 | 3.3 | 0 | 3.8 | 0
|  | 97 |  | CW | 0.8 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.71 |  | 0.5 | 4.6 | 0.9 | 0 | 1.3 | 0
ΣΔp = 95,9 kPa
Path to receptor: Ent-V. KW Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 84 |  | CW | 1.83 | 2.3 | 0.852 |  | 32 x 3,0 |  | UNIP_co |  | 1.605 | 1156.2 |  | 2.1 | 0.5 | 0.6 | 0 | 2.8 | 0
|  | 100 |  | CW | 15.94 | 1.27 | 0.619 |  | 25 x 2,5 |  | UNIP_co |  | 1.972 | 2298.32 |  | 36.6 | 0.7 | 1.4 | 0 | 38 | 0
|  | 102 |  | CW | 5.5 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.18 |  | 12 | 1.2 | 2.2 | 0 | 14.1 | 0
|  | 102_a |  | CW | 11.26 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2173.93 |  | 24.5 | 0.8 | 1.5 | 0 | 25.9 | 0
|  | 102_b |  | CW | 3.58 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2173.68 |  | 7.8 | 0.4 | 0.7 | 0 | 8.5 | 0
|  | 104 |  | CW | 0.17 | 0.9 | 0.51 |  | 25 x 2,5 |  | UNIP_co |  | 1.625 | 1631.99 |  | 0.3 | 0.8 | 1.1 | 0 | 1.3 | 0
|  | 106 |  | CW | 3.6 | 0.6 | 0.402 |  | 25 x 2,5 |  | UNIP_co |  | 1.279 | 1070.78 |  | 3.9 | 0.8 | 0.7 | 0 | 4.5 | 0
|  | 108 |  | CW | 0.68 | 0.3 | 0.3 |  | 18 x 2,0 |  | UNIP_co |  | 1.949 | 3495.36 |  | 2.4 | 1.2 | 2.3 | 0 | 4.6 | 0
ΣΔp = 155,4 kPa
Path to receptor: WT Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 84 |  | CW | 1.83 | 2.3 | 0.852 |  | 32 x 3,0 |  | UNIP_co |  | 1.605 | 1156.2 |  | 2.1 | 0.5 | 0.6 | 0 | 2.8 | 0
|  | 85 |  | CW | 4.43 | 1.03 | 0.551 |  | 25 x 2,5 |  | UNIP_co |  | 1.754 | 1869.48 |  | 8.3 | 2.6 | 4 | 0 | 12.3 | 0
|  | 87 |  | CW | 1.96 | 0.96 | 0.53 |  | 25 x 2,5 |  | UNIP_co |  | 1.686 | 1742.27 |  | 3.4 | 0.8 | 1.1 | 0 | 4.5 | 0
|  | 89 |  | CW | 0.78 | 0.66 | 0.426 |  | 25 x 2,5 |  | UNIP_co |  | 1.355 | 1185.14 |  | 0.9 | 0.8 | 0.7 | 0 | 1.7 | 0
|  | 91 |  | CW | 1.53 | 0.53 | 0.373 |  | 20 x 2,25 |  | UNIP_co |  | 1.974 | 3154.21 |  | 4.8 | 1.2 | 2.3 | 0 | 7.2 | 0
|  | 95 |  | CW | 2.49 | 0.27 | 0.238 |  | 18 x 2,0 |  | UNIP_co |  | 1.548 | 2331.74 |  | 5.8 | 0.8 | 1 | 0 | 6.8 | 0
|  | 96 |  | CW | 0.28 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1942.99 |  | 0.5 | 4.2 | 3.3 | 0 | 3.8 | 0
|  | 98 |  | CW | 0.63 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.72 |  | 0.4 | 4.6 | 0.9 | 0 | 1.2 | 0
ΣΔp = 95,8 kPa
Path to receptor: Spüle Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 31 |  | CW | 5.17 | 1.4 | 0.653 |  | 32 x 3,0 |  | UNIP_co |  | 1.231 | 723.36 |  | 3.7 | 0.7 | 0.5 | 0 | 4.3 | 0
|  | 32 |  | CW | 0.16 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.4 | 2.6 | 5 | 0 | 5.4 | 0
|  | 32_a |  | CW | 0.32 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.7 | 2.8 | 5.4 | 0 | 6.1 | 0
|  | 32_b |  | CW | 1.45 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.8 |  | 3.3 | 0 | 0 | 0 | 3.3 | 0
|  | 33 |  | CW | 0.31 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.62 |  | 0.7 | 3.2 | 5.8 | 0 | 6.4 | 0
|  | 33_a |  | CW | 0.32 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.61 |  | 0.7 | 1.6 | 2.9 | 0.1 | 3.7 | 0
|  | 48 |  | CW | 2.87 | 0.22 | 0.205 |  | 16 x 2,0 |  | UNIP_co |  | 1.813 | 3726.74 |  | 10.7 | 4.8 | 7.9 | 0 | 18.6 | 0
|  | 50 |  | CW | 2.38 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.74 |  | 1.3 | 1.6 | 0.3 | 0 | 1.7 | 0
ΣΔp = 100,4 kPa
Path to receptor: GS Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 31 |  | CW | 5.17 | 1.4 | 0.653 |  | 32 x 3,0 |  | UNIP_co |  | 1.231 | 723.36 |  | 3.7 | 0.7 | 0.5 | 0 | 4.3 | 0
|  | 32 |  | CW | 0.16 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.4 | 2.6 | 5 | 0 | 5.4 | 0
|  | 32_a |  | CW | 0.32 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.7 | 2.8 | 5.4 | 0 | 6.1 | 0
|  | 32_b |  | CW | 1.45 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.8 |  | 3.3 | 0 | 0 | 0 | 3.3 | 0
|  | 33 |  | CW | 0.31 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.62 |  | 0.7 | 3.2 | 5.8 | 0 | 6.4 | 0
|  | 33_a |  | CW | 0.32 | 1.19 | 0.598 |  | 25 x 2,5 |  | UNIP_co |  | 1.902 | 2156.61 |  | 0.7 | 1.6 | 2.9 | 0.1 | 3.7 | 0
|  | 48 |  | CW | 2.87 | 0.22 | 0.205 |  | 16 x 2,0 |  | UNIP_co |  | 1.813 | 3726.74 |  | 10.7 | 4.8 | 7.9 | 0 | 18.6 | 0
|  | 49 |  | CW | 0.53 | 0.15 | 0.15 |  | 16 x 2,0 |  | UNIP_co |  | 1.326 | 2151.52 |  | 1.1 | 5.2 | 4.6 | 0 | 5.7 | 0
ΣΔp = 104,4 kPa
Path to receptor: H 1 Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 2 |  | CW | 2.31 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.3 | 4.5 | 1.5 | 0 | 1.8 | 0
|  | 2_a |  | CW | 5.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.8 | 0 | 0 | 0 | 0.8 | 0
|  | 4 |  | CW | 3.38 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.5 | 1.8 | 0.6 | 0 | 1.1 | 0
|  | 4_a |  | CW | 4.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.7 | 1.4 | 0.5 | 0 | 1.2 | 0
|  | 4_b |  | CW | 1.53 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | 6 |  | CW | 4.16 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.6 | 0.4 | 0.1 | 0 | 0.8 | 0
|  | 14 |  | CW | 12.11 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 1.8 | 0.4 | 0.1 | 0 | 2 | 0
|  | 15 |  | CW | 4.04 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.6 | 1.7 | 0.6 | 0 | 1.2 | 0
|  | 15_a |  | CW | 0.2 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0 | 1.4 | 0.5 | 0 | 0.5 | 0
|  | 15_b |  | CW | 1.42 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | 16 |  | CW | 0.2 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0 | 1.7 | 0.6 | 0 | 0.6 | 0
|  | 16_a |  | CW | 1 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
ΣΔp = 11,0 kPa
Path to receptor: Spüle Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 31 |  | CW | 5.17 | 1.4 | 0.653 |  | 32 x 3,0 |  | UNIP_co |  | 1.231 | 723.36 |  | 3.7 | 0.7 | 0.5 | 0 | 4.3 | 0
|  | 52 |  | CW | 1.56 | 0.14 | 0.142 |  | 20 x 2,25 |  | UNIP_co |  | 0.75 | 575.81 |  | 0.9 | 4.7 | 1.3 | 0 | 2.2 | 0
|  | 52_a |  | CW | 5.48 | 0.14 | 0.142 |  | 20 x 2,25 |  | UNIP_co |  | 0.75 | 575.77 |  | 3.2 | 0 | 0 | 0 | 3.2 | 0
|  | 52_b |  | CW | 0.41 | 0.14 | 0.142 |  | 20 x 2,25 |  | UNIP_co |  | 0.75 | 575.74 |  | 0.2 | 5.6 | 1.6 | 0 | 1.8 | 0
|  | 52_c |  | CW | 8.53 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1942.6 |  | 16.6 | 4.4 | 3.4 | 0 | 20 | -0.1
|  | 52_d |  | CW | 0.51 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1942.09 |  | 1 | 0 | 0 | 0 | 1 | 0
|  | 52_e |  | CW | 3.84 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1941.96 |  | 7.5 | 0.4 | 0.3 | 0 | 7.8 | 0
|  | 53 |  | CW | 0.95 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.37 |  | 0.5 | 5.2 | 1 | 0 | 1.5 | 0
ΣΔp = 92,6 kPa
Path to receptor: Spüle Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 31 |  | CW | 5.17 | 1.4 | 0.653 |  | 32 x 3,0 |  | UNIP_co |  | 1.231 | 723.36 |  | 3.7 | 0.7 | 0.5 | 0 | 4.3 | 0
|  | 52 |  | CW | 1.56 | 0.14 | 0.142 |  | 20 x 2,25 |  | UNIP_co |  | 0.75 | 575.81 |  | 0.9 | 4.7 | 1.3 | 0 | 2.2 | 0
|  | 52_a |  | CW | 5.48 | 0.14 | 0.142 |  | 20 x 2,25 |  | UNIP_co |  | 0.75 | 575.77 |  | 3.2 | 0 | 0 | 0 | 3.2 | 0
|  | 52_b |  | CW | 0.41 | 0.14 | 0.142 |  | 20 x 2,25 |  | UNIP_co |  | 0.75 | 575.74 |  | 0.2 | 5.6 | 1.6 | 0 | 1.8 | 0
|  | 52_c |  | CW | 8.53 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1942.6 |  | 16.6 | 4.4 | 3.4 | 0 | 20 | -0.1
|  | 52_d |  | CW | 0.51 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1942.09 |  | 1 | 0 | 0 | 0 | 1 | 0
|  | 52_e |  | CW | 3.84 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1941.96 |  | 7.5 | 0.4 | 0.3 | 0 | 7.8 | 0
|  | 54 |  | CW | 1.79 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.35 |  | 1 | 1.6 | 0.3 | 0 | 1.3 | 0
ΣΔp = 92,4 kPa
Path to receptor: Spüle Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 59 |  | CW | 2.21 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.71 |  | 5.2 | 2.4 | 4.7 | 0 | 9.9 | 0
|  | 59_a |  | CW | 0.51 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.69 |  | 1.2 | 2.8 | 5.5 | 0 | 6.7 | 0
|  | 59_b |  | CW | 5.29 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.59 |  | 12.4 | 0 | 0 | 0 | 12.4 | 0
|  | 65 |  | CW | 3.29 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.63 |  | 5.6 | 3.6 | 5 | 0 | 10.6 | 0
|  | 65_a |  | CW | 0.55 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.9 | 0 | 0 | 0 | 0.9 | 0
|  | 65_b |  | CW | 0.05 | 0.94 | 0.523 |  | 25 x 2,5 |  | UNIP_co |  | 1.666 | 1705.57 |  | 0.1 | 0 | 0 | 0 | 0.1 | 0
|  | 83 |  | CW | 3.55 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.65 |  | 2 | 3 | 0.6 | 0 | 2.6 | 0
ΣΔp = 98,7 kPa
Path to receptor: WC Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 84 |  | CW | 1.83 | 2.3 | 0.852 |  | 32 x 3,0 |  | UNIP_co |  | 1.605 | 1156.2 |  | 2.1 | 0.5 | 0.6 | 0 | 2.8 | 0
|  | 85 |  | CW | 4.43 | 1.03 | 0.551 |  | 25 x 2,5 |  | UNIP_co |  | 1.754 | 1869.48 |  | 8.3 | 2.6 | 4 | 0 | 12.3 | 0
|  | 87 |  | CW | 1.96 | 0.96 | 0.53 |  | 25 x 2,5 |  | UNIP_co |  | 1.686 | 1742.27 |  | 3.4 | 0.8 | 1.1 | 0 | 4.5 | 0
|  | 89 |  | CW | 0.78 | 0.66 | 0.426 |  | 25 x 2,5 |  | UNIP_co |  | 1.355 | 1185.14 |  | 0.9 | 0.8 | 0.7 | 0 | 1.7 | 0
|  | 91 |  | CW | 1.53 | 0.53 | 0.373 |  | 20 x 2,25 |  | UNIP_co |  | 1.974 | 3154.21 |  | 4.8 | 1.2 | 2.3 | 0 | 7.2 | 0
|  | 92 |  | CW | 0.36 | 0.26 | 0.232 |  | 18 x 2,0 |  | UNIP_co |  | 1.507 | 2223.25 |  | 0.8 | 3.6 | 4.1 | 0 | 4.9 | 0
|  | 93 |  | CW | 0.55 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.79 |  | 0.9 | 4.2 | 2.8 | 0 | 3.7 | 0
ΣΔp = 92,5 kPa
Path to receptor: Spüle Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 84 |  | CW | 1.83 | 2.3 | 0.852 |  | 32 x 3,0 |  | UNIP_co |  | 1.605 | 1156.2 |  | 2.1 | 0.5 | 0.6 | 0 | 2.8 | 0
|  | 100 |  | CW | 15.94 | 1.27 | 0.619 |  | 25 x 2,5 |  | UNIP_co |  | 1.972 | 2298.32 |  | 36.6 | 0.7 | 1.4 | 0 | 38 | 0
|  | 101 |  | CW | 8.03 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.62 |  | 4.6 | 3.6 | 0.7 | 0 | 5.2 | -0.1
|  | 101_a |  | CW | 0.43 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.46 |  | 0.2 | 4.4 | 0.8 | 0 | 1.1 | 0
|  | 101_b |  | CW | 8.66 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.29 |  | 4.9 | 4.4 | 0.8 | 0 | 5.7 | -0.1
|  | 101_c |  | CW | 0.58 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.12 |  | 0.3 | 0 | 0 | 0 | 0.3 | 0
|  | 101_d |  | CW | 3.91 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.04 |  | 2.2 | 1.2 | 0.2 | 0 | 2.4 | 0
ΣΔp = 111,2 kPa
Path to receptor: Spüle Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 31 |  | CW | 5.17 | 1.4 | 0.653 |  | 32 x 3,0 |  | UNIP_co |  | 1.231 | 723.36 |  | 3.7 | 0.7 | 0.5 | 0 | 4.3 | 0
|  | 32 |  | CW | 0.16 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.4 | 2.6 | 5 | 0 | 5.4 | 0
|  | 32_a |  | CW | 0.32 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.82 |  | 0.7 | 2.8 | 5.4 | 0 | 6.1 | 0
|  | 32_b |  | CW | 1.45 | 1.26 | 0.617 |  | 25 x 2,5 |  | UNIP_co |  | 1.963 | 2280.8 |  | 3.3 | 0 | 0 | 0 | 3.3 | 0
|  | 51 |  | CW | 7.05 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.7 |  | 4 | 6.2 | 1.2 | 0 | 5.2 | -0.1
|  | 51_a |  | CW | 0.36 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.56 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | 51_b |  | CW | 5.17 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.45 |  | 2.9 | 1.2 | 0.2 | 0 | 3.2 | 0
ΣΔp = 78,5 kPa
Path to receptor: Ent-V. KW Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 84 |  | CW | 1.83 | 2.3 | 0.852 |  | 32 x 3,0 |  | UNIP_co |  | 1.605 | 1156.2 |  | 2.1 | 0.5 | 0.6 | 0 | 2.8 | 0
|  | 100 |  | CW | 15.94 | 1.27 | 0.619 |  | 25 x 2,5 |  | UNIP_co |  | 1.972 | 2298.32 |  | 36.6 | 0.7 | 1.4 | 0 | 38 | 0
|  | 102 |  | CW | 5.5 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.18 |  | 12 | 1.2 | 2.2 | 0 | 14.1 | 0
|  | 102_a |  | CW | 11.26 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2173.93 |  | 24.5 | 0.8 | 1.5 | 0 | 25.9 | 0
|  | 102_b |  | CW | 3.58 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2173.68 |  | 7.8 | 0.4 | 0.7 | 0 | 8.5 | 0
|  | 104 |  | CW | 0.17 | 0.9 | 0.51 |  | 25 x 2,5 |  | UNIP_co |  | 1.625 | 1631.99 |  | 0.3 | 0.8 | 1.1 | 0 | 1.3 | 0
|  | 105 |  | CW | 0.5 | 0.3 | 0.3 |  | 18 x 2,0 |  | UNIP_co |  | 1.949 | 3495.55 |  | 1.8 | 3.2 | 6.1 | 0 | 7.8 | 0
ΣΔp = 154,1 kPa
Path to receptor: DU Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 59 |  | CW | 2.21 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.71 |  | 5.2 | 2.4 | 4.7 | 0 | 9.9 | 0
|  | 59_a |  | CW | 0.51 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.69 |  | 1.2 | 2.8 | 5.5 | 0 | 6.7 | 0
|  | 59_b |  | CW | 5.29 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.59 |  | 12.4 | 0 | 0 | 0 | 12.4 | 0
|  | 60 |  | CW | 0.5 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 3198.61 |  | 1.6 | 3.2 | 5.5 | 0 | 7.1 | 0
|  | 60_a |  | CW | 4.55 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 3198.48 |  | 14.5 | 0.4 | 0.7 | 0 | 15.2 | 0
|  | 62 |  | CW | 2.72 | 0.22 | 0.205 |  | 16 x 2,0 |  | UNIP_co |  | 1.813 | 3726.07 |  | 10.1 | 1.8 | 3 | 0 | 13.1 | 0
|  | 63 |  | CW | 1.29 | 0.15 | 0.15 |  | 16 x 2,0 |  | UNIP_co |  | 1.326 | 2151.1 |  | 2.8 | 5.2 | 4.6 | 0 | 7.4 | 0
ΣΔp = 127,3 kPa
Path to receptor: WT Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 59 |  | CW | 2.21 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.71 |  | 5.2 | 2.4 | 4.7 | 0 | 9.9 | 0
|  | 59_a |  | CW | 0.51 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.69 |  | 1.2 | 2.8 | 5.5 | 0 | 6.7 | 0
|  | 59_b |  | CW | 5.29 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.59 |  | 12.4 | 0 | 0 | 0 | 12.4 | 0
|  | 60 |  | CW | 0.5 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 3198.61 |  | 1.6 | 3.2 | 5.5 | 0 | 7.1 | 0
|  | 60_a |  | CW | 4.55 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 3198.48 |  | 14.5 | 0.4 | 0.7 | 0 | 15.2 | 0
|  | 62 |  | CW | 2.72 | 0.22 | 0.205 |  | 16 x 2,0 |  | UNIP_co |  | 1.813 | 3726.07 |  | 10.1 | 1.8 | 3 | 0 | 13.1 | 0
|  | 64 |  | CW | 1.52 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.65 |  | 0.9 | 1.6 | 0.3 | 0 | 1.2 | 0
ΣΔp = 121,1 kPa
Path to receptor: WC Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 84 |  | CW | 1.83 | 2.3 | 0.852 |  | 32 x 3,0 |  | UNIP_co |  | 1.605 | 1156.2 |  | 2.1 | 0.5 | 0.6 | 0 | 2.8 | 0
|  | 85 |  | CW | 4.43 | 1.03 | 0.551 |  | 25 x 2,5 |  | UNIP_co |  | 1.754 | 1869.48 |  | 8.3 | 2.6 | 4 | 0 | 12.3 | 0
|  | 87 |  | CW | 1.96 | 0.96 | 0.53 |  | 25 x 2,5 |  | UNIP_co |  | 1.686 | 1742.27 |  | 3.4 | 0.8 | 1.1 | 0 | 4.5 | 0
|  | 89 |  | CW | 0.78 | 0.66 | 0.426 |  | 25 x 2,5 |  | UNIP_co |  | 1.355 | 1185.14 |  | 0.9 | 0.8 | 0.7 | 0 | 1.7 | 0
|  | 91 |  | CW | 1.53 | 0.53 | 0.373 |  | 20 x 2,25 |  | UNIP_co |  | 1.974 | 3154.21 |  | 4.8 | 1.2 | 2.3 | 0 | 7.2 | 0
|  | 92 |  | CW | 0.36 | 0.26 | 0.232 |  | 18 x 2,0 |  | UNIP_co |  | 1.507 | 2223.25 |  | 0.8 | 3.6 | 4.1 | 0 | 4.9 | 0
|  | 94 |  | CW | 1.37 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.77 |  | 2.3 | 1.4 | 0.9 | 0 | 3.2 | 0
ΣΔp = 92,1 kPa
Path to receptor: Ent-V. KW Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 24 |  | CW | 2.02 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.52 |  | 4.4 | 2.6 | 4.7 | 0 | 9.1 | 0
|  | 24_a |  | CW | 11.3 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.29 |  | 24.6 | 0.8 | 1.5 | 0 | 26 | 0
|  | 24_b |  | CW | 0.94 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.06 |  | 2.1 | 0.4 | 0.7 | 0 | 2.8 | 0
|  | 26 |  | CW | 0.12 | 0.9 | 0.51 |  | 25 x 2,5 |  | UNIP_co |  | 1.625 | 1632.3 |  | 0.2 | 0.8 | 1.1 | 0 | 1.3 | 0
|  | 28 |  | CW | 4.14 | 0.6 | 0.402 |  | 25 x 2,5 |  | UNIP_co |  | 1.279 | 1070.98 |  | 4.4 | 0.8 | 0.7 | 0 | 5.1 | 0
|  | 30 |  | CW | 0.73 | 0.3 | 0.3 |  | 18 x 2,0 |  | UNIP_co |  | 1.949 | 3496.01 |  | 2.5 | 1.2 | 2.3 | 0 | 4.8 | 0
ΣΔp = 100,0 kPa
Path to receptor: Ent-V. KW Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 24 |  | CW | 2.02 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.52 |  | 4.4 | 2.6 | 4.7 | 0 | 9.1 | 0
|  | 24_a |  | CW | 11.3 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.29 |  | 24.6 | 0.8 | 1.5 | 0 | 26 | 0
|  | 24_b |  | CW | 0.94 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.06 |  | 2.1 | 0.4 | 0.7 | 0 | 2.8 | 0
|  | 26 |  | CW | 0.12 | 0.9 | 0.51 |  | 25 x 2,5 |  | UNIP_co |  | 1.625 | 1632.3 |  | 0.2 | 0.8 | 1.1 | 0 | 1.3 | 0
|  | 28 |  | CW | 4.14 | 0.6 | 0.402 |  | 25 x 2,5 |  | UNIP_co |  | 1.279 | 1070.98 |  | 4.4 | 0.8 | 0.7 | 0 | 5.1 | 0
|  | 29 |  | CW | 0.61 | 0.3 | 0.3 |  | 18 x 2,0 |  | UNIP_co |  | 1.949 | 3496.01 |  | 2.1 | 3.2 | 6.1 | 0 | 8.2 | 0
ΣΔp = 103,4 kPa
Path to receptor: WC Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 59 |  | CW | 2.21 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.71 |  | 5.2 | 2.4 | 4.7 | 0 | 9.9 | 0
|  | 59_a |  | CW | 0.51 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.69 |  | 1.2 | 2.8 | 5.5 | 0 | 6.7 | 0
|  | 59_b |  | CW | 5.29 | 1.29 | 0.625 |  | 25 x 2,5 |  | UNIP_co |  | 1.989 | 2333.59 |  | 12.4 | 0 | 0 | 0 | 12.4 | 0
|  | 60 |  | CW | 0.5 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 3198.61 |  | 1.6 | 3.2 | 5.5 | 0 | 7.1 | 0
|  | 60_a |  | CW | 4.55 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 3198.48 |  | 14.5 | 0.4 | 0.7 | 0 | 15.2 | 0
|  | 61 |  | CW | 0.47 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.67 |  | 0.8 | 4.2 | 2.8 | 0 | 3.6 | 0
ΣΔp = 110,4 kPa
Path to receptor: Ent-V. KW Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 84 |  | CW | 1.83 | 2.3 | 0.852 |  | 32 x 3,0 |  | UNIP_co |  | 1.605 | 1156.2 |  | 2.1 | 0.5 | 0.6 | 0 | 2.8 | 0
|  | 100 |  | CW | 15.94 | 1.27 | 0.619 |  | 25 x 2,5 |  | UNIP_co |  | 1.972 | 2298.32 |  | 36.6 | 0.7 | 1.4 | 0 | 38 | 0
|  | 102 |  | CW | 5.5 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.18 |  | 12 | 1.2 | 2.2 | 0 | 14.1 | 0
|  | 102_a |  | CW | 11.26 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2173.93 |  | 24.5 | 0.8 | 1.5 | 0 | 25.9 | 0
|  | 102_b |  | CW | 3.58 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2173.68 |  | 7.8 | 0.4 | 0.7 | 0 | 8.5 | 0
|  | 103 |  | CW | 0.5 | 0.3 | 0.3 |  | 18 x 2,0 |  | UNIP_co |  | 1.949 | 3495.55 |  | 1.7 | 3.2 | 6.1 | 0 | 7.8 | 0
ΣΔp = 152,7 kPa
Path to receptor: H 2 Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 2 |  | CW | 2.31 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.3 | 4.5 | 1.5 | 0 | 1.8 | 0
|  | 2_a |  | CW | 5.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.8 | 0 | 0 | 0 | 0.8 | 0
|  | 4 |  | CW | 3.38 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.5 | 1.8 | 0.6 | 0 | 1.1 | 0
|  | 4_a |  | CW | 4.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.7 | 1.4 | 0.5 | 0 | 1.2 | 0
|  | 4_b |  | CW | 1.53 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | 6 |  | CW | 4.16 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.6 | 0.4 | 0.1 | 0 | 0.8 | 0
|  | 14 |  | CW | 12.11 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 1.8 | 0.4 | 0.1 | 0 | 2 | 0
|  | 20 |  | CW | 5.45 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 0.8 | 1.8 | 0.6 | 0 | 1.4 | 0
|  | 20_a |  | CW | 7.63 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.33 |  | 1.2 | 1.4 | 0.5 | 0 | 1.6 | 0
|  | 20_b |  | CW | 3.39 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.32 |  | 0.5 | 1.4 | 0.5 | 0 | 1 | 0
ΣΔp = 12,4 kPa
Path to receptor: WC Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 84 |  | CW | 1.83 | 2.3 | 0.852 |  | 32 x 3,0 |  | UNIP_co |  | 1.605 | 1156.2 |  | 2.1 | 0.5 | 0.6 | 0 | 2.8 | 0
|  | 85 |  | CW | 4.43 | 1.03 | 0.551 |  | 25 x 2,5 |  | UNIP_co |  | 1.754 | 1869.48 |  | 8.3 | 2.6 | 4 | 0 | 12.3 | 0
|  | 87 |  | CW | 1.96 | 0.96 | 0.53 |  | 25 x 2,5 |  | UNIP_co |  | 1.686 | 1742.27 |  | 3.4 | 0.8 | 1.1 | 0 | 4.5 | 0
|  | 89 |  | CW | 0.78 | 0.66 | 0.426 |  | 25 x 2,5 |  | UNIP_co |  | 1.355 | 1185.14 |  | 0.9 | 0.8 | 0.7 | 0 | 1.7 | 0
|  | 90 |  | CW | 0.62 | 0.13 | 0.13 |  | 16 x 2,0 |  | UNIP_co |  | 1.149 | 1673.84 |  | 1 | 3.2 | 2.1 | 0 | 3.2 | 0
ΣΔp = 79,9 kPa
Path to receptor: Ent-V. KW Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 24 |  | CW | 2.02 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.52 |  | 4.4 | 2.6 | 4.7 | 0 | 9.1 | 0
|  | 24_a |  | CW | 11.3 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.29 |  | 24.6 | 0.8 | 1.5 | 0 | 26 | 0
|  | 24_b |  | CW | 0.94 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.06 |  | 2.1 | 0.4 | 0.7 | 0 | 2.8 | 0
|  | 26 |  | CW | 0.12 | 0.9 | 0.51 |  | 25 x 2,5 |  | UNIP_co |  | 1.625 | 1632.3 |  | 0.2 | 0.8 | 1.1 | 0 | 1.3 | 0
|  | 27 |  | CW | 0.57 | 0.3 | 0.3 |  | 18 x 2,0 |  | UNIP_co |  | 1.949 | 3496.22 |  | 2 | 3.2 | 6.1 | 0 | 8.1 | 0
ΣΔp = 98,2 kPa
Path to receptor: Urinal Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 84 |  | CW | 1.83 | 2.3 | 0.852 |  | 32 x 3,0 |  | UNIP_co |  | 1.605 | 1156.2 |  | 2.1 | 0.5 | 0.6 | 0 | 2.8 | 0
|  | 85 |  | CW | 4.43 | 1.03 | 0.551 |  | 25 x 2,5 |  | UNIP_co |  | 1.754 | 1869.48 |  | 8.3 | 2.6 | 4 | 0 | 12.3 | 0
|  | 87 |  | CW | 1.96 | 0.96 | 0.53 |  | 25 x 2,5 |  | UNIP_co |  | 1.686 | 1742.27 |  | 3.4 | 0.8 | 1.1 | 0 | 4.5 | 0
|  | 88 |  | CW | 1.09 | 0.3 | 0.3 |  | 18 x 2,0 |  | UNIP_co |  | 1.949 | 3496.54 |  | 3.8 | 3.2 | 6.1 | 0 | 9.9 | 0
ΣΔp = 85,0 kPa
Path to receptor: Ent-V. KW Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 23 |  | CW | 4.8 | 2.6 | 0.908 |  | 32 x 3,0 |  | UNIP_co |  | 1.711 | 1294.85 |  | 6.2 | 2.4 | 3.5 | 0 | 9.7 | 0
|  | 24 |  | CW | 2.02 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.52 |  | 4.4 | 2.6 | 4.7 | 0 | 9.1 | 0
|  | 24_a |  | CW | 11.3 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.29 |  | 24.6 | 0.8 | 1.5 | 0 | 26 | 0
|  | 24_b |  | CW | 0.94 | 1.2 | 0.6 |  | 25 x 2,5 |  | UNIP_co |  | 1.911 | 2174.06 |  | 2.1 | 0.4 | 0.7 | 0 | 2.8 | 0
|  | 25 |  | CW | 0.56 | 0.3 | 0.3 |  | 18 x 2,0 |  | UNIP_co |  | 1.949 | 3496.23 |  | 1.9 | 3.2 | 6.1 | 0 | 8 | 0
ΣΔp = 96,9 kPa
Path to receptor: WT Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 58 |  | CW | 13.38 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.94 |  | 8.6 | 6.1 | 5.4 | 0 | 14 | 0
|  | 58_a |  | CW | 5.77 | 3.59 | 1.072 |  | 40 x 4,0 |  | UNIP_le |  | 1.333 | 644.92 |  | 3.7 | 0 | 0 | 0 | 3.7 | 0
|  | 84 |  | CW | 1.83 | 2.3 | 0.852 |  | 32 x 3,0 |  | UNIP_co |  | 1.605 | 1156.2 |  | 2.1 | 0.5 | 0.6 | 0 | 2.8 | 0
|  | 85 |  | CW | 4.43 | 1.03 | 0.551 |  | 25 x 2,5 |  | UNIP_co |  | 1.754 | 1869.48 |  | 8.3 | 2.6 | 4 | 0 | 12.3 | 0
|  | 86 |  | CW | 0.8 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 566.78 |  | 0.5 | 3.6 | 0.7 | 0 | 1.1 | 0
ΣΔp = 71,7 kPa
Path to receptor: SV 4 Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 57 |  | CW | 0.7 | 0.001 | 0.001 |  | 16 x 2,0 |  | UNIP_co |  | 0.009 | 2.7 |  | 0 | 4.4 | 0 | 0 | 0 | -0.4
ΣΔp = 57,4 kPa
Path to receptor: H 1 Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 2 |  | CW | 2.31 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.3 | 4.5 | 1.5 | 0 | 1.8 | 0
|  | 2_a |  | CW | 5.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.8 | 0 | 0 | 0 | 0.8 | 0
|  | 4 |  | CW | 3.38 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.5 | 1.8 | 0.6 | 0 | 1.1 | 0
|  | 4_a |  | CW | 4.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.7 | 1.4 | 0.5 | 0 | 1.2 | 0
|  | 4_b |  | CW | 1.53 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | 5 |  | CW | 2.49 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.34 |  | 0.4 | 1.7 | 0.6 | 0 | 0.9 | 0
ΣΔp = 6,6 kPa
Path to receptor: H 1 Type: CW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 2 |  | CW | 2.31 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.3 | 4.5 | 1.5 | 0 | 1.8 | 0
|  | 2_a |  | CW | 5.6 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.8 | 0 | 0 | 0 | 0.8 | 0
|  | 3 |  | CW | 4.69 | 0 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.35 |  | 0.7 | 1.7 | 0.6 | 0 | 1.3 | 0
ΣΔp = 4,5 kPa

## Flow paths HW
Flow paths HW
|  | Description |  | Type | L [m] | ΣVr [dm³/s] | Vs [dm³/s] |  | Diam. [mm] |  | Piperun type |  | v [m/s] | R [Pa/m] |  | R*L [kPa] | Σζ | Z [kPa] | Δparm [kPa] | Δp [kPa] | Δθ [K]
Source: no name
Path to receptor: Spüle Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H74 |  | HW | 15.12 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1289.89 |  | 19.5 | 3.9 | 5.2 | 0 | 24.7 | 0.1
|  | H74_a |  | HW | 5.77 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1290.12 |  | 7.4 | 0 | 0 | 0 | 7.4 | 0
|  | H75 |  | HW | 2.31 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.48 |  | 2 | 3.2 | 2.8 | 0 | 4.8 | 0
|  | H75_a |  | HW | 0.61 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.51 |  | 0.5 | 2.8 | 2.4 | 0 | 3 | 0
|  | H75_b |  | HW | 5.29 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.55 |  | 4.7 | 0 | 0 | 0 | 4.7 | 0
|  | H79 |  | HW | 3.29 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.31 |  | 6.2 | 1.6 | 2.3 | 0 | 8.4 | 0
|  | H80 |  | HW | 0.65 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.37 |  | 1.2 | 0 | 0 | 0 | 1.2 | 0
|  | H80_a |  | HW | 0.15 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.38 |  | 0.3 | 0 | 0 | 0 | 0.3 | 0
|  | H81 |  | HW | 2.1 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2462.73 |  | 5.2 | 3.6 | 6.1 | 0 | 11.2 | 0
|  | H83 |  | HW | 0.9 | 0.28 | 0.245 |  | 18 x 2,0 |  | UNIP_co |  | 1.589 | 1874.07 |  | 1.7 | 1 | 1.2 | 0 | 2.9 | 0
|  | H85 |  | HW | 0.91 | 0.21 | 0.198 |  | 16 x 2,0 |  | UNIP_co |  | 1.75 | 2686.06 |  | 2.4 | 1 | 1.5 | 0 | 3.9 | 0
|  | H87 |  | HW | 0.3 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1482.79 |  | 0.4 | 1.2 | 0.9 | 0 | 1.4 | 0
|  | H88 |  | HW | 1.12 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.06 |  | 0.5 | 5.2 | 1 | 0 | 1.5 | 0
ΣΔp = 147,4 kPa
Path to receptor: WT Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H74 |  | HW | 15.12 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1289.89 |  | 19.5 | 3.9 | 5.2 | 0 | 24.7 | 0.1
|  | H74_a |  | HW | 5.77 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1290.12 |  | 7.4 | 0 | 0 | 0 | 7.4 | 0
|  | H75 |  | HW | 2.31 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.48 |  | 2 | 3.2 | 2.8 | 0 | 4.8 | 0
|  | H75_a |  | HW | 0.61 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.51 |  | 0.5 | 2.8 | 2.4 | 0 | 3 | 0
|  | H75_b |  | HW | 5.29 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.55 |  | 4.7 | 0 | 0 | 0 | 4.7 | 0
|  | H79 |  | HW | 3.29 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.31 |  | 6.2 | 1.6 | 2.3 | 0 | 8.4 | 0
|  | H80 |  | HW | 0.65 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.37 |  | 1.2 | 0 | 0 | 0 | 1.2 | 0
|  | H80_a |  | HW | 0.15 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.38 |  | 0.3 | 0 | 0 | 0 | 0.3 | 0
|  | H81 |  | HW | 2.1 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2462.73 |  | 5.2 | 3.6 | 6.1 | 0 | 11.2 | 0
|  | H83 |  | HW | 0.9 | 0.28 | 0.245 |  | 18 x 2,0 |  | UNIP_co |  | 1.589 | 1874.07 |  | 1.7 | 1 | 1.2 | 0 | 2.9 | 0
|  | H85 |  | HW | 0.91 | 0.21 | 0.198 |  | 16 x 2,0 |  | UNIP_co |  | 1.75 | 2686.06 |  | 2.4 | 1 | 1.5 | 0 | 3.9 | 0
|  | H87 |  | HW | 0.3 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1482.79 |  | 0.4 | 1.2 | 0.9 | 0 | 1.4 | 0
|  | H89 |  | HW | 2.83 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.09 |  | 1.2 | 2 | 0.4 | 0 | 1.6 | 0.1
ΣΔp = 147,5 kPa
Path to receptor: WT Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H74 |  | HW | 15.12 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1289.89 |  | 19.5 | 3.9 | 5.2 | 0 | 24.7 | 0.1
|  | H74_a |  | HW | 5.77 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1290.12 |  | 7.4 | 0 | 0 | 0 | 7.4 | 0
|  | H75 |  | HW | 2.31 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.48 |  | 2 | 3.2 | 2.8 | 0 | 4.8 | 0
|  | H75_a |  | HW | 0.61 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.51 |  | 0.5 | 2.8 | 2.4 | 0 | 3 | 0
|  | H75_b |  | HW | 5.29 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.55 |  | 4.7 | 0 | 0 | 0 | 4.7 | 0
|  | H79 |  | HW | 3.29 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.31 |  | 6.2 | 1.6 | 2.3 | 0 | 8.4 | 0
|  | H80 |  | HW | 0.65 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.37 |  | 1.2 | 0 | 0 | 0 | 1.2 | 0
|  | H80_a |  | HW | 0.15 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.38 |  | 0.3 | 0 | 0 | 0 | 0.3 | 0
|  | H81 |  | HW | 2.1 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2462.73 |  | 5.2 | 3.6 | 6.1 | 0 | 11.2 | 0
|  | H83 |  | HW | 0.9 | 0.28 | 0.245 |  | 18 x 2,0 |  | UNIP_co |  | 1.589 | 1874.07 |  | 1.7 | 1 | 1.2 | 0 | 2.9 | 0
|  | H85 |  | HW | 0.91 | 0.21 | 0.198 |  | 16 x 2,0 |  | UNIP_co |  | 1.75 | 2686.06 |  | 2.4 | 1 | 1.5 | 0 | 3.9 | 0
|  | H86 |  | HW | 2.22 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.07 |  | 1 | 5.6 | 1.1 | 0 | 2 | 0.1
ΣΔp = 146,6 kPa
Path to receptor: WT Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H74 |  | HW | 15.12 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1289.89 |  | 19.5 | 3.9 | 5.2 | 0 | 24.7 | 0.1
|  | H74_a |  | HW | 5.77 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1290.12 |  | 7.4 | 0 | 0 | 0 | 7.4 | 0
|  | H75 |  | HW | 2.31 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.48 |  | 2 | 3.2 | 2.8 | 0 | 4.8 | 0
|  | H75_a |  | HW | 0.61 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.51 |  | 0.5 | 2.8 | 2.4 | 0 | 3 | 0
|  | H75_b |  | HW | 5.29 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.55 |  | 4.7 | 0 | 0 | 0 | 4.7 | 0
|  | H79 |  | HW | 3.29 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.31 |  | 6.2 | 1.6 | 2.3 | 0 | 8.4 | 0
|  | H80 |  | HW | 0.65 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.37 |  | 1.2 | 0 | 0 | 0 | 1.2 | 0
|  | H80_a |  | HW | 0.15 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.38 |  | 0.3 | 0 | 0 | 0 | 0.3 | 0
|  | H81 |  | HW | 2.1 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2462.73 |  | 5.2 | 3.6 | 6.1 | 0 | 11.2 | 0
|  | H83 |  | HW | 0.9 | 0.28 | 0.245 |  | 18 x 2,0 |  | UNIP_co |  | 1.589 | 1874.07 |  | 1.7 | 1 | 1.2 | 0 | 2.9 | 0
|  | H84 |  | HW | 2.23 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.06 |  | 1 | 4.6 | 0.9 | 0 | 1.8 | 0.1
ΣΔp = 142,4 kPa
Path to receptor: Spüle Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H58 |  | HW | 4.47 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.59 |  | 3.4 | 2.6 | 1.9 | 0 | 5.3 | 0
|  | H58_a |  | HW | 5.7 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.68 |  | 4.4 | 0 | 0 | 0 | 4.4 | 0
|  | H59 |  | HW | 0.26 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.78 |  | 0.5 | 3.2 | 4.6 | 0 | 5.1 | 0
|  | H59_a |  | HW | 0.42 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.8 |  | 0.8 | 3 | 4.3 | 0 | 5.1 | 0
|  | H59_b |  | HW | 1.46 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.83 |  | 2.7 | 0 | 0 | 0 | 2.7 | 0
|  | H60 |  | HW | 0.41 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2461.98 |  | 1 | 3.6 | 6.1 | 0 | 7.1 | 0
|  | H60_a |  | HW | 0.42 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2462.01 |  | 1 | 0 | 0 | 0 | 1 | 0
|  | H61 |  | HW | 0.32 | 0.28 | 0.245 |  | 18 x 2,0 |  | UNIP_co |  | 1.589 | 1873.46 |  | 0.6 | 3.7 | 4.6 | 0 | 5.2 | 0
|  | H62 |  | HW | 9.95 | 0.21 | 0.198 |  | 16 x 2,0 |  | UNIP_co |  | 1.75 | 2685.54 |  | 26.7 | 5.4 | 8.1 | 0 | 34.9 | 0.1
|  | H65 |  | HW | 2.78 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.06 |  | 1.2 | 6 | 1.1 | 0 | 2.3 | 0.1
ΣΔp = 145,0 kPa
Path to receptor: WT Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H58 |  | HW | 4.47 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.59 |  | 3.4 | 2.6 | 1.9 | 0 | 5.3 | 0
|  | H58_a |  | HW | 5.7 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.68 |  | 4.4 | 0 | 0 | 0 | 4.4 | 0
|  | H59 |  | HW | 0.26 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.78 |  | 0.5 | 3.2 | 4.6 | 0 | 5.1 | 0
|  | H59_a |  | HW | 0.42 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.8 |  | 0.8 | 3 | 4.3 | 0 | 5.1 | 0
|  | H59_b |  | HW | 1.46 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.83 |  | 2.7 | 0 | 0 | 0 | 2.7 | 0
|  | H60 |  | HW | 0.41 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2461.98 |  | 1 | 3.6 | 6.1 | 0 | 7.1 | 0
|  | H60_a |  | HW | 0.42 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2462.01 |  | 1 | 0 | 0 | 0 | 1 | 0
|  | H61 |  | HW | 0.32 | 0.28 | 0.245 |  | 18 x 2,0 |  | UNIP_co |  | 1.589 | 1873.46 |  | 0.6 | 3.7 | 4.6 | 0 | 5.2 | 0
|  | H62 |  | HW | 9.95 | 0.21 | 0.198 |  | 16 x 2,0 |  | UNIP_co |  | 1.75 | 2685.54 |  | 26.7 | 5.4 | 8.1 | 0 | 34.9 | 0.1
|  | H63 |  | HW | 1.06 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.03 |  | 0.5 | 6.8 | 1.3 | 0 | 1.7 | 0
ΣΔp = 144,4 kPa
Path to receptor: WT Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H58 |  | HW | 4.47 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.59 |  | 3.4 | 2.6 | 1.9 | 0 | 5.3 | 0
|  | H58_a |  | HW | 5.7 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.68 |  | 4.4 | 0 | 0 | 0 | 4.4 | 0
|  | H59 |  | HW | 0.26 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.78 |  | 0.5 | 3.2 | 4.6 | 0 | 5.1 | 0
|  | H59_a |  | HW | 0.42 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.8 |  | 0.8 | 3 | 4.3 | 0 | 5.1 | 0
|  | H59_b |  | HW | 1.46 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.83 |  | 2.7 | 0 | 0 | 0 | 2.7 | 0
|  | H60 |  | HW | 0.41 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2461.98 |  | 1 | 3.6 | 6.1 | 0 | 7.1 | 0
|  | H60_a |  | HW | 0.42 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2462.01 |  | 1 | 0 | 0 | 0 | 1 | 0
|  | H61 |  | HW | 0.32 | 0.28 | 0.245 |  | 18 x 2,0 |  | UNIP_co |  | 1.589 | 1873.46 |  | 0.6 | 3.7 | 4.6 | 0 | 5.2 | 0
|  | H66 |  | HW | 0.97 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 427.88 |  | 0.4 | 5.8 | 1.1 | 0 | 1.5 | 0
|  | H66_a |  | HW | 0.71 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 427.92 |  | 0.3 | 0 | 0 | 0 | 0.3 | 0
ΣΔp = 109,6 kPa
Path to receptor: WT Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H58 |  | HW | 4.47 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.59 |  | 3.4 | 2.6 | 1.9 | 0 | 5.3 | 0
|  | H58_a |  | HW | 5.7 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.68 |  | 4.4 | 0 | 0 | 0 | 4.4 | 0
|  | H59 |  | HW | 0.26 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.78 |  | 0.5 | 3.2 | 4.6 | 0 | 5.1 | 0
|  | H59_a |  | HW | 0.42 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.8 |  | 0.8 | 3 | 4.3 | 0 | 5.1 | 0
|  | H59_b |  | HW | 1.46 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.83 |  | 2.7 | 0 | 0 | 0 | 2.7 | 0
|  | H60 |  | HW | 0.41 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2461.98 |  | 1 | 3.6 | 6.1 | 0 | 7.1 | 0
|  | H60_a |  | HW | 0.42 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2462.01 |  | 1 | 0 | 0 | 0 | 1 | 0
|  | H61 |  | HW | 0.32 | 0.28 | 0.245 |  | 18 x 2,0 |  | UNIP_co |  | 1.589 | 1873.46 |  | 0.6 | 3.7 | 4.6 | 0 | 5.2 | 0
|  | H62 |  | HW | 9.95 | 0.21 | 0.198 |  | 16 x 2,0 |  | UNIP_co |  | 1.75 | 2685.54 |  | 26.7 | 5.4 | 8.1 | 0 | 34.9 | 0.1
|  | H64 |  | HW | 0.59 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.02 |  | 0.3 | 2.4 | 0.5 | 0 | 0.7 | 0
ΣΔp = 143,3 kPa
Path to receptor: WT Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H74 |  | HW | 15.12 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1289.89 |  | 19.5 | 3.9 | 5.2 | 0 | 24.7 | 0.1
|  | H74_a |  | HW | 5.77 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1290.12 |  | 7.4 | 0 | 0 | 0 | 7.4 | 0
|  | H75 |  | HW | 2.31 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.48 |  | 2 | 3.2 | 2.8 | 0 | 4.8 | 0
|  | H75_a |  | HW | 0.61 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.51 |  | 0.5 | 2.8 | 2.4 | 0 | 3 | 0
|  | H75_b |  | HW | 5.29 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.55 |  | 4.7 | 0 | 0 | 0 | 4.7 | 0
|  | H79 |  | HW | 3.29 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.31 |  | 6.2 | 1.6 | 2.3 | 0 | 8.4 | 0
|  | H80 |  | HW | 0.65 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.37 |  | 1.2 | 0 | 0 | 0 | 1.2 | 0
|  | H80_a |  | HW | 0.15 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.38 |  | 0.3 | 0 | 0 | 0 | 0.3 | 0
|  | H81 |  | HW | 2.1 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2462.73 |  | 5.2 | 3.6 | 6.1 | 0 | 11.2 | 0
|  | H82 |  | HW | 2.23 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.05 |  | 1 | 4.6 | 0.9 | 0 | 1.8 | 0.1
ΣΔp = 139,5 kPa
Path to receptor: Spüle Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H58 |  | HW | 4.47 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.59 |  | 3.4 | 2.6 | 1.9 | 0 | 5.3 | 0
|  | H58_a |  | HW | 5.7 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.68 |  | 4.4 | 0 | 0 | 0 | 4.4 | 0
|  | H70 |  | HW | 1.36 | 0.14 | 0.142 |  | 20 x 2,25 |  | UNIP_co |  | 0.75 | 437.45 |  | 0.6 | 3.8 | 1.1 | 0 | 1.6 | 0
|  | H70_a |  | HW | 5.38 | 0.14 | 0.142 |  | 20 x 2,25 |  | UNIP_co |  | 0.75 | 437.53 |  | 2.4 | 0 | 0 | 0 | 2.4 | 0.1
|  | H70_b |  | HW | 0.51 | 0.14 | 0.142 |  | 20 x 2,25 |  | UNIP_co |  | 0.75 | 437.61 |  | 0.2 | 5.6 | 1.5 | 0 | 1.8 | 0
|  | H70_c |  | HW | 8.53 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1482.95 |  | 12.6 | 1.2 | 0.9 | 0 | 13.6 | 0.1
|  | H71 |  | HW | 0.61 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1483.17 |  | 0.9 | 0 | 0 | 0 | 0.9 | 0
|  | H71_a |  | HW | 3.49 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1483.31 |  | 5.2 | 0.4 | 0.3 | 0 | 5.5 | 0
|  | H73 |  | HW | 1.89 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.26 |  | 0.8 | 1.6 | 0.3 | 0 | 1.1 | 0
ΣΔp = 108,4 kPa
Path to receptor: Spüle Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H74 |  | HW | 15.12 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1289.89 |  | 19.5 | 3.9 | 5.2 | 0 | 24.7 | 0.1
|  | H74_a |  | HW | 5.77 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1290.12 |  | 7.4 | 0 | 0 | 0 | 7.4 | 0
|  | H75 |  | HW | 2.31 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.48 |  | 2 | 3.2 | 2.8 | 0 | 4.8 | 0
|  | H75_a |  | HW | 0.61 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.51 |  | 0.5 | 2.8 | 2.4 | 0 | 3 | 0
|  | H75_b |  | HW | 5.29 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.55 |  | 4.7 | 0 | 0 | 0 | 4.7 | 0
|  | H79 |  | HW | 3.29 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.31 |  | 6.2 | 1.6 | 2.3 | 0 | 8.4 | 0
|  | H80 |  | HW | 0.65 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.37 |  | 1.2 | 0 | 0 | 0 | 1.2 | 0
|  | H80_a |  | HW | 0.15 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1874.38 |  | 0.3 | 0 | 0 | 0 | 0.3 | 0
|  | H90 |  | HW | 3.4 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.05 |  | 1.5 | 3.4 | 0.6 | 0 | 2.1 | 0.1
ΣΔp = 128,5 kPa
Path to receptor: Spüle Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H74 |  | HW | 15.12 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1289.89 |  | 19.5 | 3.9 | 5.2 | 0 | 24.7 | 0.1
|  | H74_a |  | HW | 5.77 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1290.12 |  | 7.4 | 0 | 0 | 0 | 7.4 | 0
|  | H91 |  | HW | 1.84 | 0.28 | 0.245 |  | 20 x 2,25 |  | UNIP_co |  | 1.296 | 1152.33 |  | 2.1 | 1.8 | 1.5 | 0 | 3.6 | 0
|  | H97 |  | HW | 15.94 | 0.07 | 0.066 |  | 20 x 2,25 |  | UNIP_co |  | 0.35 | 114.63 |  | 1.8 | 3.8 | 0.2 | 0 | 2.1 | 0.5
|  | H97_a |  | HW | 7.93 | 0.07 | 0.066 |  | 20 x 2,25 |  | UNIP_co |  | 0.35 | 114.8 |  | 0.9 | 0.4 | 0 | 0 | 0.9 | 0.2
|  | H97_b |  | HW | 0.53 | 0.07 | 0.066 |  | 20 x 2,25 |  | UNIP_co |  | 0.35 | 114.86 |  | 0.1 | 5.6 | 0.3 | 0 | 0.4 | 0
|  | H97_c |  | HW | 8.66 | 0.07 | 0.066 |  | 16 x 2,0 |  | UNIP_co |  | 0.584 | 388.18 |  | 3.4 | 1.2 | 0.2 | 0 | 3.6 | 0.2
|  | H98 |  | HW | 0.68 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 429.51 |  | 0.3 | 0 | 0 | 0 | 0.3 | 0
|  | H98_a |  | HW | 4.16 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 429.61 |  | 1.8 | 1.2 | 0.2 | 0 | 2 | 0.1
ΣΔp = 116,9 kPa
Path to receptor: Spüle Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H58 |  | HW | 4.47 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.59 |  | 3.4 | 2.6 | 1.9 | 0 | 5.3 | 0
|  | H58_a |  | HW | 5.7 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.68 |  | 4.4 | 0 | 0 | 0 | 4.4 | 0
|  | H70 |  | HW | 1.36 | 0.14 | 0.142 |  | 20 x 2,25 |  | UNIP_co |  | 0.75 | 437.45 |  | 0.6 | 3.8 | 1.1 | 0 | 1.6 | 0
|  | H70_a |  | HW | 5.38 | 0.14 | 0.142 |  | 20 x 2,25 |  | UNIP_co |  | 0.75 | 437.53 |  | 2.4 | 0 | 0 | 0 | 2.4 | 0.1
|  | H70_b |  | HW | 0.51 | 0.14 | 0.142 |  | 20 x 2,25 |  | UNIP_co |  | 0.75 | 437.61 |  | 0.2 | 5.6 | 1.5 | 0 | 1.8 | 0
|  | H70_c |  | HW | 8.53 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1482.95 |  | 12.6 | 1.2 | 0.9 | 0 | 13.6 | 0.1
|  | H71 |  | HW | 0.61 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1483.17 |  | 0.9 | 0 | 0 | 0 | 0.9 | 0
|  | H71_a |  | HW | 3.49 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1483.31 |  | 5.2 | 0.4 | 0.3 | 0 | 5.5 | 0
|  | H72 |  | HW | 1.05 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.24 |  | 0.4 | 5.2 | 1 | 0 | 1.4 | 0
ΣΔp = 108,7 kPa
Path to receptor: WT Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H74 |  | HW | 15.12 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1289.89 |  | 19.5 | 3.9 | 5.2 | 0 | 24.7 | 0.1
|  | H74_a |  | HW | 5.77 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1290.12 |  | 7.4 | 0 | 0 | 0 | 7.4 | 0
|  | H75 |  | HW | 2.31 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.48 |  | 2 | 3.2 | 2.8 | 0 | 4.8 | 0
|  | H75_a |  | HW | 0.61 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.51 |  | 0.5 | 2.8 | 2.4 | 0 | 3 | 0
|  | H75_b |  | HW | 5.29 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.55 |  | 4.7 | 0 | 0 | 0 | 4.7 | 0
|  | H76 |  | HW | 0.6 | 0.22 | 0.205 |  | 16 x 2,0 |  | UNIP_co |  | 1.813 | 2860.36 |  | 1.7 | 3.2 | 5.2 | 0 | 6.9 | 0
|  | H76_a |  | HW | 6.91 | 0.22 | 0.205 |  | 16 x 2,0 |  | UNIP_co |  | 1.813 | 2860.68 |  | 19.8 | 1.2 | 1.9 | 0 | 21.7 | 0.1
|  | H78 |  | HW | 1.67 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.09 |  | 0.7 | 1.6 | 0.3 | 0 | 1 | 0
ΣΔp = 146,1 kPa
Path to receptor: Spüle Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H58 |  | HW | 4.47 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.59 |  | 3.4 | 2.6 | 1.9 | 0 | 5.3 | 0
|  | H58_a |  | HW | 5.7 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.68 |  | 4.4 | 0 | 0 | 0 | 4.4 | 0
|  | H59 |  | HW | 0.26 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.78 |  | 0.5 | 3.2 | 4.6 | 0 | 5.1 | 0
|  | H59_a |  | HW | 0.42 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.8 |  | 0.8 | 3 | 4.3 | 0 | 5.1 | 0
|  | H59_b |  | HW | 1.46 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.83 |  | 2.7 | 0 | 0 | 0 | 2.7 | 0
|  | H68 |  | HW | 7.05 | 0.07 | 0.066 |  | 16 x 2,0 |  | UNIP_co |  | 0.584 | 386.91 |  | 2.7 | 3.4 | 0.6 | 0 | 3.3 | 0.1
|  | H69 |  | HW | 0.46 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.08 |  | 0.2 | 0 | 0 | 0 | 0.2 | 0
|  | H69_a |  | HW | 4.92 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.19 |  | 2.1 | 1.2 | 0.2 | 0 | 2.3 | 0.1
ΣΔp = 100,3 kPa
Path to receptor: DU Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H74 |  | HW | 15.12 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1289.89 |  | 19.5 | 3.9 | 5.2 | 0 | 24.7 | 0.1
|  | H74_a |  | HW | 5.77 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1290.12 |  | 7.4 | 0 | 0 | 0 | 7.4 | 0
|  | H75 |  | HW | 2.31 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.48 |  | 2 | 3.2 | 2.8 | 0 | 4.8 | 0
|  | H75_a |  | HW | 0.61 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.51 |  | 0.5 | 2.8 | 2.4 | 0 | 3 | 0
|  | H75_b |  | HW | 5.29 | 0.64 | 0.418 |  | 25 x 2,5 |  | UNIP_co |  | 1.33 | 883.55 |  | 4.7 | 0 | 0 | 0 | 4.7 | 0
|  | H76 |  | HW | 0.6 | 0.22 | 0.205 |  | 16 x 2,0 |  | UNIP_co |  | 1.813 | 2860.36 |  | 1.7 | 3.2 | 5.2 | 0 | 6.9 | 0
|  | H76_a |  | HW | 6.91 | 0.22 | 0.205 |  | 16 x 2,0 |  | UNIP_co |  | 1.813 | 2860.68 |  | 19.8 | 1.2 | 1.9 | 0 | 21.7 | 0.1
|  | H77 |  | HW | 1.39 | 0.15 | 0.15 |  | 16 x 2,0 |  | UNIP_co |  | 1.326 | 1643.41 |  | 2.3 | 5.2 | 4.5 | 0 | 6.8 | 0
ΣΔp = 151,9 kPa
Path to receptor: Spüle Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H58 |  | HW | 4.47 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.59 |  | 3.4 | 2.6 | 1.9 | 0 | 5.3 | 0
|  | H58_a |  | HW | 5.7 | 0.56 | 0.385 |  | 25 x 2,5 |  | UNIP_co |  | 1.227 | 764.68 |  | 4.4 | 0 | 0 | 0 | 4.4 | 0
|  | H59 |  | HW | 0.26 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.78 |  | 0.5 | 3.2 | 4.6 | 0 | 5.1 | 0
|  | H59_a |  | HW | 0.42 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.8 |  | 0.8 | 3 | 4.3 | 0 | 5.1 | 0
|  | H59_b |  | HW | 1.46 | 0.42 | 0.322 |  | 20 x 2,25 |  | UNIP_co |  | 1.704 | 1873.83 |  | 2.7 | 0 | 0 | 0 | 2.7 | 0
|  | H60 |  | HW | 0.41 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2461.98 |  | 1 | 3.6 | 6.1 | 0 | 7.1 | 0
|  | H60_a |  | HW | 0.42 | 0.35 | 0.285 |  | 18 x 2,0 |  | UNIP_co |  | 1.853 | 2462.01 |  | 1 | 0 | 0 | 0 | 1 | 0
|  | H67 |  | HW | 5.1 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 427.96 |  | 2.2 | 4.5 | 0.8 | 0 | 3 | 0.1
ΣΔp = 105,6 kPa
Path to receptor: WT Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H74 |  | HW | 15.12 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1289.89 |  | 19.5 | 3.9 | 5.2 | 0 | 24.7 | 0.1
|  | H74_a |  | HW | 5.77 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1290.12 |  | 7.4 | 0 | 0 | 0 | 7.4 | 0
|  | H91 |  | HW | 1.84 | 0.28 | 0.245 |  | 20 x 2,25 |  | UNIP_co |  | 1.296 | 1152.33 |  | 2.1 | 1.8 | 1.5 | 0 | 3.6 | 0
|  | H92 |  | HW | 4.63 | 0.21 | 0.198 |  | 16 x 2,0 |  | UNIP_co |  | 1.75 | 2685.62 |  | 12.4 | 3.6 | 5.4 | 0 | 17.8 | 0
|  | H94 |  | HW | 6.77 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1482.84 |  | 10 | 6 | 4.6 | 0 | 14.7 | 0.1
|  | H94_a |  | HW | 0.28 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1483.07 |  | 0.4 | 0 | 0 | 0 | 0.4 | 0
|  | H96 |  | HW | 0.9 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.14 |  | 0.4 | 4.6 | 0.9 | 0 | 1.3 | 0
ΣΔp = 141,8 kPa
Path to receptor: WT Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H74 |  | HW | 15.12 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1289.89 |  | 19.5 | 3.9 | 5.2 | 0 | 24.7 | 0.1
|  | H74_a |  | HW | 5.77 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1290.12 |  | 7.4 | 0 | 0 | 0 | 7.4 | 0
|  | H91 |  | HW | 1.84 | 0.28 | 0.245 |  | 20 x 2,25 |  | UNIP_co |  | 1.296 | 1152.33 |  | 2.1 | 1.8 | 1.5 | 0 | 3.6 | 0
|  | H92 |  | HW | 4.63 | 0.21 | 0.198 |  | 16 x 2,0 |  | UNIP_co |  | 1.75 | 2685.62 |  | 12.4 | 3.6 | 5.4 | 0 | 17.8 | 0
|  | H94 |  | HW | 6.77 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1482.84 |  | 10 | 6 | 4.6 | 0 | 14.7 | 0.1
|  | H94_a |  | HW | 0.28 | 0.14 | 0.142 |  | 16 x 2,0 |  | UNIP_co |  | 1.251 | 1483.07 |  | 0.4 | 0 | 0 | 0 | 0.4 | 0
|  | H95 |  | HW | 0.73 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428.13 |  | 0.3 | 4.6 | 0.9 | 0 | 1.2 | 0
ΣΔp = 141,7 kPa
Path to receptor: WT Type: HW
|  | no name |  | SRC |  | 7.671 | 1.66 | [11 empty] | 0 | 0
|  | 1 |  | CW | 3.33 | 7.671 | 1.66 |  | 63 x 6,0 |  | UNIP_le |  | 0.813 | 151.36 |  | 0.5 | 0 | 0 | 0 | 0.5 | 0
|  | 21 |  | CW | 1.34 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.7 | 14 | 27 | 7.2 | 35.8 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 32 |  | Δp= | 9.7 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 32 |  | Δp= | 3.9 |  | [kPa] | Setting:
|  | 21_a |  | CW | 1.16 | 7.671 | 1.566 |  | 40 x 4,0 |  | UNIP_le |  | 1.947 | 1262.32 |  | 1.5 | 0 | 0 | 0 | 1.5 | 0
|  | 22 |  | CW | 1.74 | 4.081 | 1.144 |  | 40 x 4,0 |  | UNIP_le |  | 1.423 | 723.58 |  | 1.3 | 2.1 | 2.1 | 0 | 3.4 | 0
|  | 55 |  | CW | 3.61 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.6 |  | 2.8 | 2.8 | 2.3 | 0 | 5 | 0
|  | 55_a |  | CW | 2.62 | 1.481 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.59 |  | 2 | 10.7 | 9.3 | 0 | 11.3 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  |  | Valve: | NR valve |  |  |  | Diameter: |  | 25 |  | Δp= | 3.8 |  | [kPa] | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.8 |  | [kPa] | Setting:
|  | 56 |  | CW | 1.19 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 763.09 |  | 0.9 | 2.3 | 1.9 | 0 | 2.8 | 0
|  | Speicher TWE |  | HTR |  | 1.48 | 0.674 | [9 empty] | 1.5 | 1.2 |  | 1.2 | 0
|  | H57 |  | HW | 4.26 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.55 |  | 2.5 | 7.4 | 6 | 0 | 8.5 | 0
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= | 1.7 |  | [kPa] | Setting:
|  | H57_a |  | HW | 3.36 | 1.48 | 0.674 |  | 32 x 3,0 |  | UNIP_co |  | 1.269 | 589.58 |  | 2 | 0 | 0 | 0 | 2 | 0
|  | H74 |  | HW | 15.12 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1289.89 |  | 19.5 | 3.9 | 5.2 | 0 | 24.7 | 0.1
|  | H74_a |  | HW | 5.77 | 0.92 | 0.517 |  | 25 x 2,5 |  | UNIP_co |  | 1.645 | 1290.12 |  | 7.4 | 0 | 0 | 0 | 7.4 | 0
|  | H91 |  | HW | 1.84 | 0.28 | 0.245 |  | 20 x 2,25 |  | UNIP_co |  | 1.296 | 1152.33 |  | 2.1 | 1.8 | 1.5 | 0 | 3.6 | 0
|  | H92 |  | HW | 4.63 | 0.21 | 0.198 |  | 16 x 2,0 |  | UNIP_co |  | 1.75 | 2685.62 |  | 12.4 | 3.6 | 5.4 | 0 | 17.8 | 0
|  | H93 |  | HW | 1.1 | 0.07 | 0.07 |  | 16 x 2,0 |  | UNIP_co |  | 0.619 | 428 |  | 0.5 | 5.6 | 1.1 | 0 | 1.5 | 0
ΣΔp = 127,0 kPa

## Circulation circuits
Circulation circuits
|  | Description |  | Type | L [m] | VsCirc [dm³/s] | Diam. [mm] |  | Piperun type |  | v [m/s] |  | R [Pa/m] |  | R*L [kPa] |  | Σζ |  | Z [kPa] | Δparm [kPa] | Δp [kPa]
Source: no name
Circulation circuit: H59_b
|  | Speicher TWE |  | HTR |  | 0.09 | [14 empty] | 0,00
|  | H57 |  | HW | 4.26 | 0.09 | 32 x 3,0 |  | UNIP_co |  | 0.17 |  | 16.98 |  | 0.07 |  | 7.4 |  | 0.08 | 0 | 0,15
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= |  | 1.7 |  | [kPa] |  | Setting:
|  | H57_a |  | HW | 3.36 | 0.09 | 32 x 3,0 |  | UNIP_co |  | 0.17 |  | 16.99 |  | 0.06 |  | 0 |  | 0 | 0 | 0,06
|  | H58 |  | HW | 4.47 | 0.045 | 25 x 2,5 |  | UNIP_co |  | 0.144 |  | 17.57 |  | 0.08 |  | 2.6 |  | 0.03 | 0 | 0,11
|  | H58_a |  | HW | 5.7 | 0.045 | 25 x 2,5 |  | UNIP_co |  | 0.144 |  | 17.59 |  | 0.1 |  | 0 |  | 0 | 0 | 0,10
|  | H59 |  | HW | 0.26 | 0.023 | 20 x 2,25 |  | UNIP_co |  | 0.12 |  | 17.61 |  | 0 |  | 3.2 |  | 0.02 | 0 | 0,03
|  | H59_a |  | HW | 0.42 | 0.023 | 20 x 2,25 |  | UNIP_co |  | 0.12 |  | 17.61 |  | 0.01 |  | 3 |  | 0.02 | 0 | 0,03
|  | H59_b |  | HW | 1.46 | 0.023 | 20 x 2,25 |  | UNIP_co |  | 0.12 |  | 17.62 |  | 0.03 |  | 0 |  | 0 | 0 | 0,03
|  | H68 |  | HW | 7.05 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.36 |  | 0.42 |  | 3.4 |  | 0.07 | 0 | 0,49
|  | CCP | [18 empty] | -0,04
|  | H59_c |  | Circ | 0.1 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.41 |  | 0.01 |  | 0 |  | 0 | 0 | 0,01
|  | H59_b |  | Circ | 8.6 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.47 |  | 0.51 |  | 4.4 |  | 0.09 | 0 | 0,60
|  | H59_a |  | Circ | 0.52 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.53 |  | 0.03 |  | 4.4 |  | 0.09 | 0 | 0,12
|  | H59 |  | Circ | 0.36 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.54 |  | 0.02 |  | 5.2 |  | 0.1 | 0 | 0,12
|  | H58 |  | Circ | 10.38 | 0.045 | 16 x 2,0 |  | UNIP_co |  | 0.4 |  | 200.71 |  | 2.08 |  | 3.6 |  | 0.28 | 0 | 2,37
|  | H57_a |  | Circ | 3.64 | 0.09 | 20 x 2,25 |  | UNIP_co |  | 0.48 |  | 201.96 |  | 0.73 |  | 0 |  | 0 | 0 | 0,73
|  | H57 |  | Circ | 3.88 | 0.09 | 20 x 2,25 |  | UNIP_co |  | 0.48 |  | 202.02 |  | 0.78 |  | 15.3 |  | 1.83 | -12.11 | -9,49
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 20 |  | Δp= |  | 0.3 |  | [kPa] |  | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 15 |  | Δp= |  | 0.9 |  | [kPa] |  | Setting:
|  |  | Pump: | no name |  |  |  | Vs= | 0.09 | [dm³/s] |  | H= | 12.1 |  | [kPa]
ΣΔp = -4,61 kPa
Circulation circuit: H70_b
|  | Speicher TWE |  | HTR |  | 0.09 | [14 empty] | 0,00
|  | H57 |  | HW | 4.26 | 0.09 | 32 x 3,0 |  | UNIP_co |  | 0.17 |  | 16.98 |  | 0.07 |  | 7.4 |  | 0.08 | 0 | 0,15
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= |  | 1.7 |  | [kPa] |  | Setting:
|  | H57_a |  | HW | 3.36 | 0.09 | 32 x 3,0 |  | UNIP_co |  | 0.17 |  | 16.99 |  | 0.06 |  | 0 |  | 0 | 0 | 0,06
|  | H58 |  | HW | 4.47 | 0.045 | 25 x 2,5 |  | UNIP_co |  | 0.144 |  | 17.57 |  | 0.08 |  | 2.6 |  | 0.03 | 0 | 0,11
|  | H58_a |  | HW | 5.7 | 0.045 | 25 x 2,5 |  | UNIP_co |  | 0.144 |  | 17.59 |  | 0.1 |  | 0 |  | 0 | 0 | 0,10
|  | H70 |  | HW | 1.36 | 0.023 | 20 x 2,25 |  | UNIP_co |  | 0.12 |  | 17.61 |  | 0.02 |  | 3.8 |  | 0.03 | 0 | 0,05
|  | H70_a |  | HW | 5.38 | 0.023 | 20 x 2,25 |  | UNIP_co |  | 0.12 |  | 17.63 |  | 0.09 |  | 0 |  | 0 | 0 | 0,09
|  | H70_b |  | HW | 0.51 | 0.023 | 20 x 2,25 |  | UNIP_co |  | 0.12 |  | 17.65 |  | 0.01 |  | 5.6 |  | 0.04 | 0 | 0,05
|  | H70_c |  | HW | 8.53 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.5 |  | 0.51 |  | 1.2 |  | 0.02 | 0 | 0,53
|  | CCP | [18 empty] | -0,04
|  | H60_d |  | Circ | 0.1 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.56 |  | 0.01 |  | 0 |  | 0 | 0 | 0,01
|  | H60_c |  | Circ | 8.63 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.61 |  | 0.51 |  | 4.4 |  | 0.09 | 0 | 0,60
|  | H60_b |  | Circ | 0.61 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.68 |  | 0.04 |  | 4.4 |  | 0.09 | 0 | 0,12
|  | H60_a |  | Circ | 5.28 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.74 |  | 0.32 |  | 0 |  | 0 | 0 | 0,32
|  | H60 |  | Circ | 1.16 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.8 |  | 0.07 |  | 5.6 |  | 0.11 | 0 | 0,18
|  | H58 |  | Circ | 10.38 | 0.045 | 16 x 2,0 |  | UNIP_co |  | 0.4 |  | 200.71 |  | 2.08 |  | 3.6 |  | 0.28 | 0 | 2,37
|  | H57_a |  | Circ | 3.64 | 0.09 | 20 x 2,25 |  | UNIP_co |  | 0.48 |  | 201.96 |  | 0.73 |  | 0 |  | 0 | 0 | 0,73
|  | H57 |  | Circ | 3.88 | 0.09 | 20 x 2,25 |  | UNIP_co |  | 0.48 |  | 202.02 |  | 0.78 |  | 15.3 |  | 1.83 | -12.11 | -9,49
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 20 |  | Δp= |  | 0.3 |  | [kPa] |  | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 15 |  | Δp= |  | 0.9 |  | [kPa] |  | Setting:
|  |  | Pump: | no name |  |  |  | Vs= | 0.09 | [dm³/s] |  | H= | 12.1 |  | [kPa]
ΣΔp = -4,07 kPa
Circulation circuit: H75_b
|  | Speicher TWE |  | HTR |  | 0.09 | [14 empty] | 0,00
|  | H57 |  | HW | 4.26 | 0.09 | 32 x 3,0 |  | UNIP_co |  | 0.17 |  | 16.98 |  | 0.07 |  | 7.4 |  | 0.08 | 0 | 0,15
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= |  | 1.7 |  | [kPa] |  | Setting:
|  | H57_a |  | HW | 3.36 | 0.09 | 32 x 3,0 |  | UNIP_co |  | 0.17 |  | 16.99 |  | 0.06 |  | 0 |  | 0 | 0 | 0,06
|  | H74 |  | HW | 15.12 | 0.045 | 25 x 2,5 |  | UNIP_co |  | 0.144 |  | 17.59 |  | 0.27 |  | 3.9 |  | 0.04 | 0 | 0,31
|  | H74_a |  | HW | 5.77 | 0.045 | 25 x 2,5 |  | UNIP_co |  | 0.144 |  | 17.63 |  | 0.1 |  | 0 |  | 0 | 0 | 0,10
|  | H75 |  | HW | 2.31 | 0.023 | 25 x 2,5 |  | UNIP_co |  | 0.072 |  | 5.27 |  | 0.01 |  | 3.2 |  | 0.01 | 0 | 0,02
|  | H75_a |  | HW | 0.61 | 0.023 | 25 x 2,5 |  | UNIP_co |  | 0.072 |  | 5.28 |  | 0 |  | 2.8 |  | 0.01 | 0 | 0,01
|  | H75_b |  | HW | 5.29 | 0.023 | 25 x 2,5 |  | UNIP_co |  | 0.072 |  | 5.28 |  | 0.03 |  | 0 |  | 0 | 0 | 0,03
|  | H79 |  | HW | 3.29 | 0.023 | 20 x 2,25 |  | UNIP_co |  | 0.12 |  | 17.7 |  | 0.06 |  | 1.6 |  | 0.01 | 0 | 0,07
|  | CCP | [18 empty] | -0,06
|  | H62_c |  | Circ | 0.1 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.63 |  | 0.01 |  | 0 |  | 0 | 0 | 0,01
|  | H62_b |  | Circ | 8.68 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.69 |  | 0.52 |  | 4.4 |  | 0.09 | 0 | 0,60
|  | H62_a |  | Circ | 0.71 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.75 |  | 0.04 |  | 4.4 |  | 0.09 | 0 | 0,13
|  | H62 |  | Circ | 2.41 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 59.78 |  | 0.14 |  | 5.2 |  | 0.1 | 0 | 0,25
|  | H61_a |  | Circ | 5.77 | 0.045 | 16 x 2,0 |  | UNIP_co |  | 0.4 |  | 202.53 |  | 1.17 |  | 0 |  | 0 | 0 | 1,17
|  | H61 |  | Circ | 15.12 | 0.045 | 16 x 2,0 |  | UNIP_co |  | 0.4 |  | 202.86 |  | 3.07 |  | 5.6 |  | 0.44 | 0 | 3,51
|  | H57_a |  | Circ | 3.64 | 0.09 | 20 x 2,25 |  | UNIP_co |  | 0.48 |  | 201.96 |  | 0.73 |  | 0 |  | 0 | 0 | 0,73
|  | H57 |  | Circ | 3.88 | 0.09 | 20 x 2,25 |  | UNIP_co |  | 0.48 |  | 202.02 |  | 0.78 |  | 15.3 |  | 1.83 | -12.11 | -9,49
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 20 |  | Δp= |  | 0.3 |  | [kPa] |  | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 15 |  | Δp= |  | 0.9 |  | [kPa] |  | Setting:
|  |  | Pump: | no name |  |  |  | Vs= | 0.09 | [dm³/s] |  | H= | 12.1 |  | [kPa]
ΣΔp = -2,41 kPa
Circulation circuit: H97_b
|  | Speicher TWE |  | HTR |  | 0.09 | [14 empty] | 0,00
|  | H57 |  | HW | 4.26 | 0.09 | 32 x 3,0 |  | UNIP_co |  | 0.17 |  | 16.98 |  | 0.07 |  | 7.4 |  | 0.08 | 0 | 0,15
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 25 |  | Δp= |  | 1.7 |  | [kPa] |  | Setting:
|  | H57_a |  | HW | 3.36 | 0.09 | 32 x 3,0 |  | UNIP_co |  | 0.17 |  | 16.99 |  | 0.06 |  | 0 |  | 0 | 0 | 0,06
|  | H74 |  | HW | 15.12 | 0.045 | 25 x 2,5 |  | UNIP_co |  | 0.144 |  | 17.59 |  | 0.27 |  | 3.9 |  | 0.04 | 0 | 0,31
|  | H74_a |  | HW | 5.77 | 0.045 | 25 x 2,5 |  | UNIP_co |  | 0.144 |  | 17.63 |  | 0.1 |  | 0 |  | 0 | 0 | 0,10
|  | H91 |  | HW | 1.84 | 0.023 | 20 x 2,25 |  | UNIP_co |  | 0.12 |  | 17.65 |  | 0.03 |  | 1.8 |  | 0.01 | 0 | 0,05
|  | H97 |  | HW | 15.94 | 0.023 | 20 x 2,25 |  | UNIP_co |  | 0.12 |  | 17.71 |  | 0.28 |  | 3.8 |  | 0.03 | 0 | 0,31
|  | H97_a |  | HW | 7.93 | 0.023 | 20 x 2,25 |  | UNIP_co |  | 0.12 |  | 17.79 |  | 0.14 |  | 0.4 |  | 0 | 0 | 0,14
|  | H97_b |  | HW | 0.53 | 0.023 | 20 x 2,25 |  | UNIP_co |  | 0.12 |  | 17.82 |  | 0.01 |  | 5.6 |  | 0.04 | 0 | 0,05
|  | H97_c |  | HW | 8.66 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 60.06 |  | 0.52 |  | 1.2 |  | 0.02 | 0 | 0,54
|  | CCP | [18 empty] | -0,04
|  | H63_d |  | Circ | 0.1 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 60.11 |  | 0.01 |  | 0 |  | 0 | 0 | 0,01
|  | H63_c |  | Circ | 8.76 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 60.17 |  | 0.53 |  | 4.4 |  | 0.09 | 0 | 0,61
|  | H63_b |  | Circ | 0.63 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 60.23 |  | 0.04 |  | 4.4 |  | 0.09 | 0 | 0,12
|  | H63_a |  | Circ | 7.83 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 60.31 |  | 0.47 |  | 0.4 |  | 0.01 | 0 | 0,48
|  | H63 |  | Circ | 17.78 | 0.023 | 16 x 2,0 |  | UNIP_co |  | 0.2 |  | 60.55 |  | 1.08 |  | 5.6 |  | 0.11 | 0 | 1,19
|  | H61_a |  | Circ | 5.77 | 0.045 | 16 x 2,0 |  | UNIP_co |  | 0.4 |  | 202.53 |  | 1.17 |  | 0 |  | 0 | 0 | 1,17
|  | H61 |  | Circ | 15.12 | 0.045 | 16 x 2,0 |  | UNIP_co |  | 0.4 |  | 202.86 |  | 3.07 |  | 5.6 |  | 0.44 | 0 | 3,51
|  | H57_a |  | Circ | 3.64 | 0.09 | 20 x 2,25 |  | UNIP_co |  | 0.48 |  | 201.96 |  | 0.73 |  | 0 |  | 0 | 0 | 0,73
|  | H57 |  | Circ | 3.88 | 0.09 | 20 x 2,25 |  | UNIP_co |  | 0.48 |  | 202.02 |  | 0.78 |  | 15.3 |  | 1.83 | -12.11 | -9,49
|  |  | Valve: | Shutoff valve with NR va |  |  |  | Diameter: |  | 20 |  | Δp= |  | 0.3 |  | [kPa] |  | Setting:
|  |  | Valve: | Shutoff valve, incl. |  |  |  | Diameter: |  | 15 |  | Δp= |  | 0.9 |  | [kPa] |  | Setting:
|  |  | Pump: | no name |  |  |  | Vs= | 0.09 | [dm³/s] |  | H= | 12.1 |  | [kPa]
ΣΔp = 0,00 kPa

## Comp. list CW
Component list on CW pipe-runs
|  | Catalogue name | Component name | Cat. code | ζ | kv | Press. drop [kPa]
Group: "Ungrouped"
Pipe-run 1:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | 79 33 01 | - | - | 0
Pipe-run 2:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 1 | 1.7 | - | 0.6
Pipe-run 2_a:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | 79 33 01 | - | - | 0
Pipe-run 3:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 2_a | 1.7 | - | 0.6
Pipe-run 4:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 2_a | 0.4 | - | 0.1
Pipe-run 4_a:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
Pipe-run 4_b:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | 79 33 01 | - | - | 0
Pipe-run 5:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 4_b | 1.7 | - | 0.6
Pipe-run 6:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | 79 33 01 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 4_b | 0.4 | - | 0.1
Pipe-run 7:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 6 | 1.7 | - | 0.6
Pipe-run 14:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | 79 33 01 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 6 | 0.4 | - | 0.1
Pipe-run 15:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 14 | 1.7 | - | 0.6
Pipe-run 20:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 14 | 0.4 | - | 0.1
Pipe-run 20_a:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
Pipe-run 20_b:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
Pipe-run 21:, UNIPIPE white, supplied in straight lengths40 x 4,0, Vs: 1,566 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 63 - 40 | 79 43 03 | 0.6 | - | 1.1
|  | UPONOR - UNIPIPE | Male press connection 40 - 1_1/4"MT | 90 72 50 | 0.4 | - | 0.8
|  | Miscellaneous fittings of any make | Shutoff valve, inclined, acc. to DIN 1988 32 | Shutoff valve, inclined DN32 | 2 | - | 3.9
|  | UPONOR - UNIPIPE | Male press connection 40 - 1_1/4"MT | 90 72 50 | 0.4 | - | 0.8
|  | Brass and steel pipe couplings and fittings | Flange PN10 F50 PN10 | DN50_10 | - | - | 0
|  | Brass and steel pipe couplings and fittings | Female connector, reduction, imperial 2"MT - 1_1/2"FT |  | 0.4 | - | 0.8
|  | UPONOR - UNIPIPE | Male press connection 40 - 1_1/2"MT | 90 72 60 | 0.4 | - | 0.8
|  | Miscellaneous fittings of any make | Water meter CW MZ F50 PN10, Qnom: 20,0 m³/h | Water meter CW MZ 20.0 | - | 63.25 | 0.8
|  | Brass and steel pipe couplings and fittings | Flange PN10 F50 PN10 | DN50_10 | - | - | 0
|  | Brass and steel pipe couplings and fittings | Female connector, reduction, imperial 2"MT - 1_1/2"FT |  | 0.4 | - | 0.8
|  | UPONOR - UNIPIPE | Male press connection 40 - 1_1/2"MT | 90 72 60 | 0.4 | - | 0.8
|  | UPONOR - UNIPIPE | Male press connection 40 - 1_1/4"MT | 90 72 50 | 0.4 | - | 0.8
|  | Miscellaneous fittings of any make | Shutoff valve with non-return valve acc. to DIN 32 | Shutoff valve with non-return valve DN32 | 5 | - | 9.7
|  | Brass and steel pipe couplings and fittings | Nipple, straight, imperial 1_1/4"MT - 1_1/4"MT |  | 0.4 | - | 0.8
|  | Miscellaneous fittings of any make | FV trap 1_1/4"FT |  | - | 22.36 | 6.4
|  | Brass and steel pipe couplings and fittings | Nipple, straight, imperial 1_1/4"MT - 1_1/4"MT |  | 0.4 | - | 0.8
|  | Miscellaneous fittings of any make | Shutoff valve, inclined, acc. to DIN 1988 32 | Shutoff valve, inclined DN32 | 2 | - | 3.9
|  | UPONOR - UNIPIPE | Male press connection 40 - 1_1/4"MT | 90 72 50 | 0.4 | - | 0.8
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 1 | 0.4 | - | 0.8
Pipe-run 21_a:, UNIPIPE white, supplied in straight lengths40 x 4,0, Vs: 1,566 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 40 - 40 - 40 | 93 71 77 | - | - | 0
Pipe-run 22:, UNIPIPE white, supplied in straight lengths40 x 4,0, Vs: 1,144 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 40 - 32 - 32 | 93 71 66 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 40 - 40 - 40 | Comp. on piperun 21_a | 2.1 | - | 2.1
Pipe-run 23:, UNIPIPE white, supplied in coils32 x 3,0, Vs: 0,908 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 32 - 25 - 32 | 93 61 56 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 40 - 32 - 32 | Comp. on piperun 22 | 2.4 | - | 3.5
Pipe-run 24:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,600 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 32 - 25 - 32 | Comp. on piperun 23 | 2.6 | - | 4.7
Pipe-run 31:, UNIPIPE white, supplied in coils32 x 3,0, Vs: 0,653 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 32 - 25 - 25 | 93 61 55 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 32 - 25 - 32 | Comp. on piperun 23 | 0.7 | - | 0.5
Pipe-run 32:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,617 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 32 - 25 - 25 | Comp. on piperun 31 | 2.6 | - | 5
Pipe-run 52:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,142 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 25 - 20 | 94 51 40 | 1 | - | 0.3
|  | UPONOR - UNIPIPE | Press elbow 90° 20 - 20 | 91 41 40 | 3 | - | 0.8
|  | UPONOR - UNIPIPE | Press tee 32 - 25 - 25 | Comp. on piperun 31 | 0.7 | - | 0.2
Pipe-run 52_a:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,142 [dm³/s]
Pipe-run 55:, UNIPIPE white, supplied in coils32 x 3,0, Vs: 0,674 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 32 - 32 | 91 61 60 | 2.3 | - | 1.9
|  | UPONOR - UNIPIPE | Press tee 40 - 32 - 32 | Comp. on piperun 22 | 0.5 | - | 0.4
Pipe-run 55_a:, UNIPIPE white, supplied in coils32 x 3,0, Vs: 0,674 [dm³/s]
|  | UPONOR - UNIPIPE | Male press connection 32 - 1"MT | 90 62 40 | 0.4 | - | 0.3
|  | Miscellaneous fittings of any make | Shutoff valve, inclined, acc. to DIN 1988 25 | Shutoff valve, inclined DN25 | 2 | - | 1.8
|  | UPONOR - UNIPIPE | Male press connection 32 - 1"MT | 90 62 40 | 0.4 | - | 0.3
|  | UPONOR - UNIPIPE | Male press connection 32 - 1"MT | 90 62 40 | 0.4 | - | 0.3
|  | Miscellaneous fittings of any make | Non-return screw valve acc. to DIN 1988 25 | Non-return screw valve DN25 | 4.3 | - | 3.8
|  | UPONOR - UNIPIPE | Male press connection 32 - 1"MT | 90 62 40 | 0.4 | - | 0.3
|  | UPONOR - UNIPIPE | Male press connection 32 - 1"MT | 90 62 40 | 0.4 | - | 0.3
|  | Miscellaneous fittings of any make | Shutoff valve, inclined, acc. to DIN 1988 25 | Shutoff valve, inclined DN25 | 2 | - | 1.8
|  | UPONOR - UNIPIPE | Male press connection 32 - 1"MT | 90 62 40 | 0.4 | - | 0.3
|  | UPONOR - UNIPIPE | Press tee 32 - 32 - 32 | 93 61 66 | - | - | 0
Pipe-run 56:, UNIPIPE white, supplied in coils32 x 3,0, Vs: 0,674 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 32 - 32 - 32 | Comp. on piperun 55_a | 2.3 | - | 1.9
Pipe-run 57:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,001 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 32 - 20 | 94 61 40 | 0.9 | - | 0
|  | UPONOR - UNIPIPE | Press coupling/reduction 20 - 16 | 94 41 20 | 1.2 | - | 0
|  | UPONOR - UNIPIPE | Press tee 32 - 32 - 32 | Comp. on piperun 55_a | 2.3 | - | 0
Pipe-run 58:, UNIPIPE white, supplied in straight lengths40 x 4,0, Vs: 1,072 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 40 - 40 | 91 71 70 | 2 | - | 1.8
|  | UPONOR - UNIPIPE | Press elbow 90° 40 - 40 | 91 71 70 | 2 | - | 1.8
|  | UPONOR - UNIPIPE | Press tee 40 - 40 - 40 | Comp. on piperun 21_a | 2.1 | - | 1.9
Pipe-run 58_a:, UNIPIPE white, supplied in straight lengths40 x 4,0, Vs: 1,072 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 40 - 25 - 32 | 93 71 56 | - | - | 0
Pipe-run 59:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,625 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 40 - 25 - 32 | Comp. on piperun 58_a | 2.4 | - | 4.7
Pipe-run 84:, UNIPIPE white, supplied in coils32 x 3,0, Vs: 0,852 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 32 - 25 - 25 | 93 61 55 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 40 - 25 - 32 | Comp. on piperun 58_a | 0.5 | - | 0.6
Pipe-run 85:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,551 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 25 | 93 51 25 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 32 - 25 - 25 | Comp. on piperun 84 | 2.6 | - | 4
Pipe-run 86:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 25 | Comp. on piperun 85 | 3.2 | - | 0.6
Pipe-run 87:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,530 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | 93 51 35 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 25 | Comp. on piperun 85 | 0.8 | - | 1.1
Pipe-run 88:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,300 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | Comp. on piperun 87 | 3.2 | - | 6.1
Pipe-run 89:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,426 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 20 | 93 51 24 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | Comp. on piperun 87 | 0.8 | - | 0.7
Pipe-run 90:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 20 | Comp. on piperun 89 | 3.2 | - | 2.1
Pipe-run 91:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,373 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.8
|  | UPONOR - UNIPIPE | Press tee 20 - 18 - 18 | 93 41 33 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 20 | Comp. on piperun 89 | 0.8 | - | 1.6
Pipe-run 92:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,232 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | 93 31 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 20 - 18 - 18 | Comp. on piperun 91 | 3.6 | - | 4.1
Pipe-run 93:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun 92 | 4.2 | - | 2.8
Pipe-run 94:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.3
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun 92 | 1 | - | 0.7
Pipe-run 95:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,238 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | 93 31 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 20 - 18 - 18 | Comp. on piperun 91 | 0.8 | - | 1
Pipe-run 96:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,142 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun 95 | 4.2 | - | 3.3
Pipe-run 97:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 96 | 4.6 | - | 0.9
Pipe-run 98:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 96 | 4.6 | - | 0.9
Pipe-run 99:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 2.9
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun 95 | 1 | - | 0.7
Pipe-run 99_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
Pipe-run 100:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,619 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 25 | 93 51 25 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 32 - 25 - 25 | Comp. on piperun 84 | 0.7 | - | 1.4
Pipe-run 101:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 25 | Comp. on piperun 100 | 3.2 | - | 0.6
Pipe-run 102:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,600 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.7
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 25 | Comp. on piperun 100 | 0.8 | - | 1.5
Group: "Ungrouped"
Pipe-run 16_a:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
Pipe-run 33_a:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,598 [dm³/s]
|  | Brass and steel pipe couplings and fittings | Flange PN10 F50 PN10 | DN50_10 | - | - | 0
|  | Brass and steel pipe couplings and fittings | Female connector, reduction, imperial 2"MT - 1"FT |  | 0.4 | - | 0.7
|  | UPONOR - UNIPIPE | Male press connection 25 - 1"MT | 90 52 40 | 0.4 | - | 0.7
|  | Miscellaneous fittings of any make | Water meter CW MZ F50 PN10, Qnom: 20,0 m³/h | Water meter CW MZ 20.0 | - | 63.25 | 0.1
|  | Brass and steel pipe couplings and fittings | Flange PN10 F50 PN10 | DN50_10 | - | - | 0
|  | Brass and steel pipe couplings and fittings | Nipple, reduction, imperial 2"MT - 1_1/2"MT |  | 0.4 | - | 0.7
|  | UPONOR - UNIPIPE | Female press connection 50 - 1_1/2"FT | 90 83 60 | 0.4 | - | 0.7
|  | UPONOR - UNIPIPE | Press tee 32 - 50 - 32 | 93 61 86 | - | - | 0
Pipe-run 34:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,533 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 32 - 25 | 94 61 50 | 0.9 | - | 1.3
|  | UPONOR - UNIPIPE | Press tee 25 - 25 - 25 | 93 51 55 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 32 - 50 - 32 | Comp. on piperun 33_a | 2.3 | - | 3.3
Pipe-run 35:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,466 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.4
|  |  | Elbow on drawing |  | 0.4 | - | 0.4
|  | UPONOR - UNIPIPE | Press tee 25 - 20 - 20 | 93 51 44 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 25 - 25 | Comp. on piperun 34 | 3.2 | - | 3.5
Pipe-run 36:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,300 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 20 - 18 | 94 41 30 | 1.2 | - | 2.3
|  | UPONOR - UNIPIPE | Press tee 25 - 20 - 20 | Comp. on piperun 35 | 3.2 | - | 6.1
Pipe-run 37:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,346 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 20 - 16 - 20 | 93 41 24 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 20 - 20 | Comp. on piperun 35 | 0.8 | - | 1.3
Pipe-run 38:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,198 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 20 - 16 - 20 | Comp. on piperun 37 | 3.6 | - | 5.5
Pipe-run 39:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 38 | 1.2 | - | 0.2
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 38 | 5.2 | - | 1
Pipe-run 40:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 38 | 1.2 | - | 0.2
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 38 | 1.2 | - | 0.2
Pipe-run 41:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 38 | 5.2 | - | 1
Pipe-run 42:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,232 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 20 - 18 | 94 41 30 | 1.2 | - | 1.4
|  |  | Elbow on drawing |  | 0.4 | - | 0.5
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | 93 31 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 20 - 16 - 20 | Comp. on piperun 37 | 0.8 | - | 0.9
Pipe-run 43:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun 42 | 4.2 | - | 2.8
Pipe-run 44:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.3
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun 42 | 1 | - | 0.7
Pipe-run 45:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,191 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 25 - 16 | 94 51 20 | 1 | - | 1.4
|  |  | Elbow on drawing |  | 0.4 | - | 0.6
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 25 - 25 | Comp. on piperun 34 | 0.8 | - | 1.1
Pipe-run 46:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 45 | 5.2 | - | 1
Pipe-run 47:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 2.9
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 45 | 1.2 | - | 0.8
Pipe-run 47_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
Pipe-run 48:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,205 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 32 - 20 | 94 61 40 | 0.9 | - | 1.5
|  | UPONOR - UNIPIPE | Press coupling/reduction 20 - 16 | 94 41 20 | 1.2 | - | 2
|  |  | Elbow on drawing |  | 0.4 | - | 0.7
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 32 - 50 - 32 | Comp. on piperun 33_a | 2.3 | - | 3.8
Pipe-run 49:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,150 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 48 | 5.2 | - | 4.6
Pipe-run 50:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 48 | 1.2 | - | 0.2
Group: "Ungrouped"
Pipe-run 7_d:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | 79 33 01 | - | - | 0
Pipe-run 8:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | 79 33 01 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 7_d | 1.5 | - | 0.5
Pipe-run 9:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 8 | 1.7 | - | 0.6
Pipe-run 10:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 8 | 0.4 | - | 0.1
Pipe-run 11:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | 79 33 01 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 7_d | 1.5 | - | 0.5
Pipe-run 12:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 11 | 1.7 | - | 0.6
Pipe-run 13:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 11 | 0.4 | - | 0.1
Pipe-run 18_a:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
Pipe-run 60_a:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,285 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.7
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | 93 31 22 | - | - | 0
Pipe-run 61:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun 60_a | 4.2 | - | 2.8
Pipe-run 62:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,205 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.7
|  |  | Elbow on drawing |  | 0.4 | - | 0.7
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun 60_a | 1 | - | 1.6
Pipe-run 63:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,150 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 62 | 5.2 | - | 4.6
Pipe-run 64:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 62 | 1.2 | - | 0.2
Group: "Ungrouped"
Pipe-run 10_b:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
Pipe-run 12_b:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
Pipe-run 19_a:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
Pipe-run 51_b:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
Pipe-run 52_e:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,142 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.3
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
Pipe-run 53:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 52_e | 5.2 | - | 1
Pipe-run 54:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 52_e | 1.2 | - | 0.2
Pipe-run 65_b:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,523 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 25 - 25 | 93 51 55 | - | - | 0
Pipe-run 66:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,501 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 25 | 93 51 25 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 25 - 25 | Comp. on piperun 65_b | 3.2 | - | 4.1
Pipe-run 67:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,191 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 25 | Comp. on piperun 66 | 3.2 | - | 4.5
Pipe-run 68:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 67 | 5.2 | - | 3.4
Pipe-run 69:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 67 | 1.2 | - | 0.2
Pipe-run 70:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,430 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 20 | 93 51 24 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 25 | Comp. on piperun 66 | 0.8 | - | 0.7
Pipe-run 71:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,191 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 20 | Comp. on piperun 70 | 3.2 | - | 4.5
Pipe-run 72:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 71 | 5.2 | - | 3.4
Pipe-run 73:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 71 | 1.2 | - | 0.2
Pipe-run 74:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,346 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 20 - 16 - 20 | 93 41 24 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 20 | Comp. on piperun 70 | 0.8 | - | 1.3
Pipe-run 75:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,191 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 20 - 16 - 20 | Comp. on piperun 74 | 3.6 | - | 5.1
Pipe-run 76:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 75 | 5.2 | - | 3.4
Pipe-run 77:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 75 | 1.2 | - | 0.2
Pipe-run 78:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,238 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 20 - 18 | 94 41 30 | 1.2 | - | 1.4
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | 93 31 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 20 - 16 - 20 | Comp. on piperun 74 | 0.8 | - | 1
Pipe-run 79:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun 78 | 4.2 | - | 0.8
Pipe-run 80:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,191 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.6
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun 78 | 1 | - | 1.4
Pipe-run 81:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,130 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 80 | 5.2 | - | 3.4
Pipe-run 82:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun 80 | 1.2 | - | 0.2
Pipe-run 83:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 25 - 16 | 94 51 20 | 1 | - | 0.2
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 25 - 25 - 25 | Comp. on piperun 65_b | 0.8 | - | 0.2
Pipe-run 101_d:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
Group: "Ungrouped"
Pipe-run 7_a:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
Pipe-run 7_b:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
Pipe-run 7_c:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
Pipe-run 10_a:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
Pipe-run 12_a:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
Pipe-run 15_a:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
Pipe-run 15_b:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | 79 33 01 | - | - | 0
Pipe-run 16:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 15_b | 1.7 | - | 0.6
Pipe-run 17:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | 79 33 01 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 15_b | 0.4 | - | 0.1
Pipe-run 18:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 17 | 1.7 | - | 0.6
Pipe-run 19:, UNIPIPE white, supplied in straight lengths63 x 6,0, Vs: 1,660 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 63 - 63 | 79 13 01 | 1.4 | - | 0.5
|  | UPONOR - UNIPIPE | Press tee 63 - 63 - 63 | Comp. on piperun 17 | 0.4 | - | 0.1
Pipe-run 24_a:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,600 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.7
|  |  | Elbow on drawing |  | 0.4 | - | 0.7
Pipe-run 32_a:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,617 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 25 - 25 | 91 51 50 | 2.8 | - | 5.4
Pipe-run 32_b:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,617 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 25 - 25 | 93 51 55 | - | - | 0
Pipe-run 33:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,598 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 25 - 25 | Comp. on piperun 32_b | 3.2 | - | 5.8
Pipe-run 51:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 25 - 16 | 94 51 20 | 1 | - | 0.2
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.8
|  | UPONOR - UNIPIPE | Press tee 25 - 25 - 25 | Comp. on piperun 32_b | 0.8 | - | 0.2
Pipe-run 51_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
Pipe-run 52_b:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,142 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 20 - 16 | 94 41 20 | 1.2 | - | 0.3
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 1.2
Pipe-run 52_c:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,142 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 3.4
Pipe-run 52_d:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,142 [dm³/s]
Pipe-run 59_a:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,625 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 25 - 25 | 91 51 50 | 2.8 | - | 5.5
Pipe-run 59_b:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,625 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | 93 51 35 | - | - | 0
Pipe-run 60:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,285 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | Comp. on piperun 59_b | 3.2 | - | 5.5
Pipe-run 65:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,523 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 25 - 25 | 91 51 50 | 2.8 | - | 3.9
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | Comp. on piperun 59_b | 0.8 | - | 1.1
Pipe-run 65_a:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,523 [dm³/s]
Pipe-run 101_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.8
Pipe-run 101_b:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.8
Pipe-run 101_c:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
Pipe-run 102_a:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,600 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.7
|  |  | Elbow on drawing |  | 0.4 | - | 0.7
Group: "Ungrouped"
Pipe-run 24_b:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,600 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.7
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | 93 51 35 | - | - | 0
Pipe-run 25:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,300 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | Comp. on piperun 24_b | 3.2 | - | 6.1
Pipe-run 26:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,510 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | 93 51 35 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | Comp. on piperun 24_b | 0.8 | - | 1.1
Pipe-run 27:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,300 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | Comp. on piperun 26 | 3.2 | - | 6.1
Pipe-run 28:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,402 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 18 | 93 51 33 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | Comp. on piperun 26 | 0.8 | - | 0.7
Pipe-run 29:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,300 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 18 | Comp. on piperun 28 | 3.2 | - | 6.1
Pipe-run 30:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,300 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.8
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 18 | Comp. on piperun 28 | 0.8 | - | 1.5
Pipe-run 102_b:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,600 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.7
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | 93 51 35 | - | - | 0
Pipe-run 103:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,300 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | Comp. on piperun 102_b | 3.2 | - | 6.1
Pipe-run 104:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,510 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | 93 51 35 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | Comp. on piperun 102_b | 0.8 | - | 1.1
Pipe-run 105:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,300 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | Comp. on piperun 104 | 3.2 | - | 6.1
Pipe-run 106:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,402 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 18 | 93 51 33 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 25 | Comp. on piperun 104 | 0.8 | - | 0.7
Pipe-run 107:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,300 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 18 | Comp. on piperun 106 | 3.2 | - | 6.1
Pipe-run 108:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,300 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.8
|  | UPONOR - UNIPIPE | Press tee 25 - 18 - 18 | Comp. on piperun 106 | 0.8 | - | 1.5

## Comp. list HW
Component list on HW pipe-runs
|  | Catalogue name | Component name | Cat. code | ζ | kv | Press. drop [kPa]
Group: "Ungrouped"
Pipe-run H57:, UNIPIPE white, supplied in coils32 x 3,0, Vs: 0,674 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 32 - 32 | 91 61 60 | 2.3 | - | 1.8
|  | UPONOR - UNIPIPE | Male press connection 32 - 1"MT | 90 62 40 | 0.4 | - | 0.3
|  | Miscellaneous fittings of any make | Shutoff valve, inclined, acc. to DIN 1988 25 | Shutoff valve, inclined DN25 | 2 | - | 1.7
|  | UPONOR - UNIPIPE | Male press connection 32 - 1"MT | 90 62 40 | 0.4 | - | 0.3
|  | UPONOR - UNIPIPE | Press elbow 90° 32 - 32 | 91 61 60 | 2.3 | - | 1.8
Pipe-run H57_a:, UNIPIPE white, supplied in coils32 x 3,0, Vs: 0,674 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 32 - 25 - 25 | 93 61 55 | - | - | 0
Pipe-run H58:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,385 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 32 - 25 - 25 | Comp. on piperun H57_a | 2.6 | - | 1.9
Pipe-run H58_a:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,385 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 20 - 20 | 93 51 44 | - | - | 0
Pipe-run H59:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,322 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 20 - 20 | Comp. on piperun H58_a | 3.2 | - | 4.6
Pipe-run H70:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,142 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 20 - 20 | 91 41 40 | 3 | - | 0.8
|  | UPONOR - UNIPIPE | Press tee 25 - 20 - 20 | Comp. on piperun H58_a | 0.8 | - | 0.2
Pipe-run H70_a:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,142 [dm³/s]
Pipe-run H74:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,517 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.5
|  | UPONOR - UNIPIPE | Press elbow 90° 25 - 25 | 91 51 50 | 2.8 | - | 3.7
|  | UPONOR - UNIPIPE | Press tee 32 - 25 - 25 | Comp. on piperun H57_a | 0.7 | - | 0.9
Pipe-run H74_a:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,517 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 25 - 25 | 93 51 55 | - | - | 0
Pipe-run H75:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,418 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 25 - 25 | Comp. on piperun H74_a | 3.2 | - | 2.8
Pipe-run H91:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,245 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 25 - 20 | 94 51 40 | 1 | - | 0.8
|  | UPONOR - UNIPIPE | Press tee 20 - 16 - 20 | 93 41 24 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 25 - 25 - 25 | Comp. on piperun H74_a | 0.8 | - | 0.7
Pipe-run H92:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,198 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 20 - 16 - 20 | Comp. on piperun H91 | 3.6 | - | 5.4
Pipe-run H93:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H92 | 5.2 | - | 1
Pipe-run H94:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,142 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.3
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 3.4
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H92 | 1.2 | - | 0.9
Pipe-run H94_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,142 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
Pipe-run H95:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H94_a | 4.6 | - | 0.9
Pipe-run H96:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H94_a | 4.6 | - | 0.9
Pipe-run H97:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,066 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 20 - 20 | 91 41 40 | 3 | - | 0.2
|  | UPONOR - UNIPIPE | Press tee 20 - 16 - 20 | Comp. on piperun H91 | 0.8 | - | 0
Pipe-run H97_a:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,066 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0
Group: "Ungrouped"
Pipe-run H60_a:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,285 [dm³/s]
|  |  | Water meter |  | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 18 - 18 - 16 | 93 31 32 | - | - | 0
Pipe-run H61:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,245 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | 93 31 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 18 - 18 - 16 | Comp. on piperun H60_a | 3.7 | - | 4.6
Pipe-run H62:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,198 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.6
|  |  | Elbow on drawing |  | 0.4 | - | 0.6
|  |  | Elbow on drawing |  | 0.4 | - | 0.6
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun H61 | 4.2 | - | 6.3
Pipe-run H63:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H62 | 1.2 | - | 0.2
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H62 | 5.2 | - | 1
Pipe-run H64:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H62 | 1.2 | - | 0.2
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H62 | 1.2 | - | 0.2
Pipe-run H65:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H62 | 5.2 | - | 1
Pipe-run H66:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.8
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun H61 | 1 | - | 0.2
Pipe-run H66_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
Pipe-run H67:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 18 - 18 - 16 | Comp. on piperun H60_a | 3.7 | - | 0.7
Group: "Ungrouped"
Pipe-run H76_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,205 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.6
|  |  | Elbow on drawing |  | 0.4 | - | 0.6
|  |  | Elbow on drawing |  | 0.4 | - | 0.6
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
Pipe-run H77:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,150 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H76_a | 5.2 | - | 4.5
Pipe-run H78:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H76_a | 1.2 | - | 0.2
Group: "Ungrouped"
Pipe-run H69_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
Pipe-run H71_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,142 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.3
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
Pipe-run H72:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H71_a | 5.2 | - | 1
Pipe-run H73:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H71_a | 1.2 | - | 0.2
Pipe-run H80_a:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,322 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 20 - 18 - 18 | 93 41 33 | - | - | 0
Pipe-run H81:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,285 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 18 | 93 31 23 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 20 - 18 - 18 | Comp. on piperun H80_a | 3.6 | - | 6.1
Pipe-run H82:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 18 | Comp. on piperun H81 | 4.2 | - | 0.8
Pipe-run H83:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,245 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | 93 31 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 18 | Comp. on piperun H81 | 1 | - | 1.2
Pipe-run H84:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun H83 | 4.2 | - | 0.8
Pipe-run H85:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,198 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 18 - 16 - 16 | Comp. on piperun H83 | 1 | - | 1.5
Pipe-run H86:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H85 | 5.2 | - | 1
Pipe-run H87:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,142 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H85 | 1.2 | - | 0.9
Pipe-run H88:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H87 | 5.2 | - | 1
Pipe-run H89:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H87 | 1.2 | - | 0.2
Pipe-run H90:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 18 - 16 | 94 31 20 | 1.4 | - | 0.3
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  | UPONOR - UNIPIPE | Press tee 20 - 18 - 18 | Comp. on piperun H80_a | 0.8 | - | 0.2
Pipe-run H98_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
|  |  | Elbow on drawing |  | 0.4 | - | 0.1
Group: "Ungrouped"
Pipe-run H59_a:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,322 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 20 - 20 | 91 41 40 | 3 | - | 4.3
Pipe-run H59_b:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,322 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 20 - 18 - 18 | 93 41 33 | - | - | 0
Pipe-run H60:, UNIPIPE white, supplied in coils18 x 2,0, Vs: 0,285 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 20 - 18 - 18 | Comp. on piperun H59_b | 3.6 | - | 6.1
Pipe-run H68:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,066 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 18 - 16 | 94 31 20 | 1.4 | - | 0.2
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | 1.2 | - | 0.2
|  | UPONOR - UNIPIPE | Press tee 20 - 18 - 18 | Comp. on piperun H59_b | 0.8 | - | 0.1
Pipe-run H69:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
Pipe-run H70_b:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,142 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 20 - 16 | 94 41 20 | 1.2 | - | 0.3
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 1.2
Pipe-run H70_c:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,142 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | 1.2 | - | 0.9
Pipe-run H71:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,142 [dm³/s]
Pipe-run H75_a:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,418 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 25 - 25 | 91 51 50 | 2.8 | - | 2.4
Pipe-run H75_b:, UNIPIPE white, supplied in coils25 x 2,5, Vs: 0,418 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 20 | 93 51 24 | - | - | 0
Pipe-run H76:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,205 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 20 | Comp. on piperun H75_b | 3.2 | - | 5.2
Pipe-run H79:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,322 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 20 - 20 - 16 | 93 41 42 | 0.8 | - | 1.1
|  | UPONOR - UNIPIPE | Press tee 25 - 16 - 20 | Comp. on piperun H75_b | 0.8 | - | 1.1
Pipe-run H80:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,322 [dm³/s]
Pipe-run H97_b:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,066 [dm³/s]
|  | UPONOR - UNIPIPE | Press coupling/reduction 20 - 16 | 94 41 20 | 1.2 | - | 0.1
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.3
Pipe-run H97_c:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,066 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | 1.2 | - | 0.2
Pipe-run H98:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,070 [dm³/s]
Group: "Ungrouped"

## Comp. list circ.
Component list on circ. pipe-runs
|  | Catalogue name | Component name | Cat. code | ζ | kv | Press. drop [kPa]
Group: "Ungrouped"
Pipe-run H58:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,045 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
|  | UPONOR - UNIPIPE | Press tee 20 - 16 - 16 | Comp. on piperun H57_a | 3.6 | - | 0.28
Pipe-run H57:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,090 [dm³/s]
|  | UPONOR - UNIPIPE | Female press connection 20 - 1"FT | 90 43 40 | 0.4 | - | 0.05
|  |  | Elbow on drawing |  | 0.4 | - | 0.05
|  | UPONOR - UNIPIPE | Male press connection 20 - 3/4"MT | 90 42 30 | 0.4 | - | 0.05
|  | Miscellaneous fittings of any make | Shutoff valve with non-return valve acc. to DIN 20 | Shutoff valve with non-return valve DN20 | 6 | - | 0.29
|  | UPONOR - UNIPIPE | Male press connection 20 - 3/4"MT | 90 42 30 | 0.4 | - | 0.05
|  | UPONOR - UNIPIPE | Male press connection 20 - 1/2"MT | 90 42 20 | 0.4 | - | 0.05
|  |  | Pump |  | - | - | -12.11
|  | Brass and steel pipe couplings and fittings | Nipple, straight, imperial 1/2"MT - 1/2"MT |  | 0.4 | - | 0.05
|  | Miscellaneous fittings of any make | Shutoff valve, inclined, acc. to DIN 1988 15 | Shutoff valve, inclined DN15 | 3.5 | - | 0.88
|  | UPONOR - UNIPIPE | Male press connection 20 - 1/2"MT | 90 42 20 | 0.4 | - | 0.05
|  | UPONOR - UNIPIPE | Press elbow 90° 20 - 20 | 91 41 40 | 3 | - | 0.34
Pipe-run H62:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H61_a | 5.2 | - | 0.1
Pipe-run H63:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.09
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H61_a | 1.2 | - | 0.02
Pipe-run H60_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
Pipe-run H59:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H58 | 5.2 | - | 0.1
Pipe-run H63_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.01
Pipe-run H57_a:, UNIPIPE white, supplied in coils20 x 2,25, Vs: 0,090 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 20 - 16 - 16 | 93 41 22 | - | - | 0
Pipe-run H60:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.09
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | Comp. on piperun H58 | 1.2 | - | 0.02
Pipe-run H61_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,045 [dm³/s]
|  | UPONOR - UNIPIPE | Press tee 16 - 16 - 16 | 93 21 22 | - | - | 0
Pipe-run H61:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,045 [dm³/s]
|  |  | Elbow on drawing |  | 0.4 | - | 0.03
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.35
|  | UPONOR - UNIPIPE | Press tee 20 - 16 - 16 | Comp. on piperun H57_a | 0.8 | - | 0.06
Group: "Ungrouped"
Group: "Ungrouped"
Group: "Ungrouped"
Group: "Ungrouped"
Pipe-run H63_b:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.09
Pipe-run H60_c:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.09
Pipe-run H62_c:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
Pipe-run H63_c:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.09
Pipe-run H62_b:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.09
Pipe-run H59_c:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
Pipe-run H59_b:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.09
Pipe-run H62_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.09
Pipe-run H63_d:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
Pipe-run H59_a:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.09
Pipe-run H60_b:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
|  | UPONOR - UNIPIPE | Press elbow 90° 16 - 16 | 91 21 20 | 4.4 | - | 0.09
Pipe-run H60_d:, UNIPIPE white, supplied in coils16 x 2,0, Vs: 0,023 [dm³/s]
Group: "Ungrouped"

## Heaters
Heaters
Heater | CPRNo. | ΣVr [dm³/s] | Vs [dm³/s] | Press. drop [kPa] | Circ.pr.drop [kPa] | VsCirc [dm³/s] | Circ. pump press. [kPa] | Circ.Temp [°C]
Speicher TWE | 56 | 1.48 | 0.674 | 1.2 | 0 | 0.09 | - | 55.9

## Cold water pipe-runs
| ## |  |  | CPRNo. | L [m] | ΣVr [dm³/s] | Vs [dm³/s] | Diameter |  | Piperun type | v [m/s] |  | R [Pa/m] |  | R*L [kPa] |  | Σζ | Z [kPa] | Δparm [kPa] | Δp [kPa] | Insul. [mm]
Group: "Ungrouped"
| 1 |  |  | (So.) | 3.33 | 7.671 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.36 |  | 0.5 |  | 0 | 0 | 0 | 0.5 | 0
| 2 |  |  | 1 | 2.31 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.35 |  | 0.3 |  | 4.5 | 1.5 | 0 | 1.8 | 10
| 2_a |  |  | 2 | 5.6 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.35 |  | 0.8 |  | 0 | 0 | 0 | 0.8 | 10
| 3 |  |  | 2_a | 4.69 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.35 |  | 0.7 |  | 1.7 | 0.6 | 0 | 1.3 | 10
| 4 |  |  | 2_a | 3.38 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.35 |  | 0.5 |  | 1.8 | 0.6 | 0 | 1.1 | 10
| 4_a |  |  | 4 | 4.6 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.35 |  | 0.7 |  | 1.4 | 0.5 | 0 | 1.2 | 10
| 4_b |  |  | 4_a | 1.53 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.35 |  | 0.2 |  | 0 | 0 | 0 | 0.2 | 10
| 5 |  |  | 4_b | 2.49 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.34 |  | 0.4 |  | 1.7 | 0.6 | 0 | 0.9 | 10
| 6 |  |  | 4_b | 4.16 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.34 |  | 0.6 |  | 0.4 | 0.1 | 0 | 0.8 | 10
| 7 |  |  | 6 | 2.07 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.34 |  | 0.3 |  | 1.7 | 0.6 | 0 | 0.9 | 10
| 14 |  |  | 6 | 12.11 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.34 |  | 1.8 |  | 0.4 | 0.1 | 0 | 2 | 10
| 15 |  |  | 14 | 4.04 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 0.6 |  | 1.7 | 0.6 | 0 | 1.2 | 10
| 20 |  |  | 14 | 5.45 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 0.8 |  | 1.8 | 0.6 | 0 | 1.4 | 10
| 20_a |  |  | 20 | 7.63 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 1.2 |  | 1.4 | 0.5 | 0 | 1.6 | 10
| 20_b |  |  | 20_a | 3.39 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.32 |  | 0.5 |  | 1.4 | 0.5 | 0 | 1 | 10
| 21 |  |  | 1 | 1.34 | 7.671 | 1.566 | 40 x 4,0 |  | UNIP_le | 1.947 |  | 1262.32 |  | 1.7 |  | 14 | 27 | 7.2 | 35.8 | 10
|  | Valve: | Shutoff valve, incl. | [5 empty] | Diameter: | 32 | Δp= | 3.9 |  | [kPa] |  | Setting:
|  | Valve: | Shutoff valve with NR va | [5 empty] | Diameter: | 32 | Δp= | 9.7 |  | [kPa] |  | Setting:
|  | Valve: | Shutoff valve, incl. | [5 empty] | Diameter: | 32 | Δp= | 3.9 |  | [kPa] |  | Setting:
| 21_a |  |  | 21 | 1.16 | 7.671 | 1.566 | 40 x 4,0 |  | UNIP_le | 1.947 |  | 1262.32 |  | 1.5 |  | 0 | 0 | 0 | 1.5 | 10
| 22 |  |  | 21_a | 1.74 | 4.081 | 1.144 | 40 x 4,0 |  | UNIP_le | 1.423 |  | 723.58 |  | 1.3 |  | 2.1 | 2.1 | 0 | 3.4 | 10
| 23 |  |  | 22 | 4.8 | 2.6 | 0.908 | 32 x 3,0 |  | UNIP_co | 1.711 |  | 1294.85 |  | 6.2 |  | 2.4 | 3.5 | 0 | 9.7 | 10
| 24 |  |  | 23 | 2.02 | 1.2 | 0.6 | 25 x 2,5 |  | UNIP_co | 1.911 |  | 2174.52 |  | 4.4 |  | 2.6 | 4.7 | 0 | 9.1 | 10
| 31 |  |  | 23 | 5.17 | 1.4 | 0.653 | 32 x 3,0 |  | UNIP_co | 1.231 |  | 723.36 |  | 3.7 |  | 0.7 | 0.5 | 0 | 4.3 | 10
| 32 |  |  | 31 | 0.16 | 1.26 | 0.617 | 25 x 2,5 |  | UNIP_co | 1.963 |  | 2280.82 |  | 0.4 |  | 2.6 | 5 | 0 | 5.4 | 10
| 52 |  |  | 31 | 1.56 | 0.14 | 0.142 | 20 x 2,25 |  | UNIP_co | 0.75 |  | 575.81 |  | 0.9 |  | 4.7 | 1.3 | 0 | 2.2 | 10
| 52_a |  |  | 52 | 5.48 | 0.14 | 0.142 | 20 x 2,25 |  | UNIP_co | 0.75 |  | 575.77 |  | 3.2 |  | 0 | 0 | 0 | 3.2 | 10
| 55 |  |  | 22 | 3.61 | 1.481 | 0.674 | 32 x 3,0 |  | UNIP_co | 1.269 |  | 763.6 |  | 2.8 |  | 2.8 | 2.3 | 0 | 5 | 10
| 55_a |  |  | 55 | 2.62 | 1.481 | 0.674 | 32 x 3,0 |  | UNIP_co | 1.269 |  | 763.59 |  | 2 |  | 10.7 | 9.3 | 0 | 11.3 | 10
|  | Valve: | Shutoff valve, incl. | [5 empty] | Diameter: | 25 | Δp= | 1.8 |  | [kPa] |  | Setting:
|  | Valve: | Shutoff valve, incl. | [5 empty] | Diameter: | 25 | Δp= | 1.8 |  | [kPa] |  | Setting:
|  | Valve: | NR valve | [5 empty] | Diameter: | 25 | Δp= | 3.8 |  | [kPa] |  | Setting:
| 56 |  |  | 55_a | 1.19 | 1.48 | 0.674 | 32 x 3,0 |  | UNIP_co | 1.269 |  | 763.09 |  | 0.9 |  | 2.3 | 1.9 | 0 | 2.8 | 10
| 57 |  |  | 55_a | 0.7 | 0.001 | 0.001 | 16 x 2,0 |  | UNIP_co | 0.009 |  | 2.7 |  | 0 |  | 4.4 | 0 | 0 | 0 | 10
| 58 |  |  | 21_a | 13.38 | 3.59 | 1.072 | 40 x 4,0 |  | UNIP_le | 1.333 |  | 644.94 |  | 8.6 |  | 6.1 | 5.4 | 0 | 14 | 10
| 58_a |  |  | 58 | 5.77 | 3.59 | 1.072 | 40 x 4,0 |  | UNIP_le | 1.333 |  | 644.92 |  | 3.7 |  | 0 | 0 | 0 | 3.7 | 10
| 59 |  |  | 58_a | 2.21 | 1.29 | 0.625 | 25 x 2,5 |  | UNIP_co | 1.989 |  | 2333.71 |  | 5.2 |  | 2.4 | 4.7 | 0 | 9.9 | 10
| 84 |  |  | 58_a | 1.83 | 2.3 | 0.852 | 32 x 3,0 |  | UNIP_co | 1.605 |  | 1156.2 |  | 2.1 |  | 0.5 | 0.6 | 0 | 2.8 | 10
| 85 |  |  | 84 | 4.43 | 1.03 | 0.551 | 25 x 2,5 |  | UNIP_co | 1.754 |  | 1869.48 |  | 8.3 |  | 2.6 | 4 | 0 | 12.3 | 10
| 86 |  |  | 85 | 0.8 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.78 |  | 0.5 |  | 3.6 | 0.7 | 0 | 1.1 | 10
| 87 |  |  | 85 | 1.96 | 0.96 | 0.53 | 25 x 2,5 |  | UNIP_co | 1.686 |  | 1742.27 |  | 3.4 |  | 0.8 | 1.1 | 0 | 4.5 | 10
| 88 |  |  | 87 | 1.09 | 0.3 | 0.3 | 18 x 2,0 |  | UNIP_co | 1.949 |  | 3496.54 |  | 3.8 |  | 3.2 | 6.1 | 0 | 9.9 | 10
| 89 |  |  | 87 | 0.78 | 0.66 | 0.426 | 25 x 2,5 |  | UNIP_co | 1.355 |  | 1185.14 |  | 0.9 |  | 0.8 | 0.7 | 0 | 1.7 | 10
| 90 |  |  | 89 | 0.62 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.84 |  | 1 |  | 3.2 | 2.1 | 0 | 3.2 | 10
| 91 |  |  | 89 | 1.53 | 0.53 | 0.373 | 20 x 2,25 |  | UNIP_co | 1.974 |  | 3154.21 |  | 4.8 |  | 1.2 | 2.3 | 0 | 7.2 | 10
| 92 |  |  | 91 | 0.36 | 0.26 | 0.232 | 18 x 2,0 |  | UNIP_co | 1.507 |  | 2223.25 |  | 0.8 |  | 3.6 | 4.1 | 0 | 4.9 | 10
| 93 |  |  | 92 | 0.55 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.79 |  | 0.9 |  | 4.2 | 2.8 | 0 | 3.7 | 10
| 94 |  |  | 92 | 1.37 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.77 |  | 2.3 |  | 1.4 | 0.9 | 0 | 3.2 | 10
| 95 |  |  | 91 | 2.49 | 0.27 | 0.238 | 18 x 2,0 |  | UNIP_co | 1.548 |  | 2331.74 |  | 5.8 |  | 0.8 | 1 | 0 | 6.8 | 10
| 96 |  |  | 95 | 0.28 | 0.14 | 0.142 | 16 x 2,0 |  | UNIP_co | 1.251 |  | 1942.99 |  | 0.5 |  | 4.2 | 3.3 | 0 | 3.8 | 10
| 97 |  |  | 96 | 0.8 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.71 |  | 0.5 |  | 4.6 | 0.9 | 0 | 1.3 | 10
| 98 |  |  | 96 | 0.63 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.72 |  | 0.4 |  | 4.6 | 0.9 | 0 | 1.2 | 10
| 99 |  |  | 95 | 2.24 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.67 |  | 3.8 |  | 5.4 | 3.6 | 0 | 7.3 | 10
| 99_a |  |  | 99 | 0.55 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.59 |  | 0.9 |  | 0 | 0 | 0 | 0.9 | 10
| 100 |  |  | 84 | 15.94 | 1.27 | 0.619 | 25 x 2,5 |  | UNIP_co | 1.972 |  | 2298.32 |  | 36.6 |  | 0.7 | 1.4 | 0 | 38 | 10
| 101 |  |  | 100 | 8.03 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.62 |  | 4.6 |  | 3.6 | 0.7 | 0 | 5.2 | 10
| 102 |  |  | 100 | 5.5 | 1.2 | 0.6 | 25 x 2,5 |  | UNIP_co | 1.911 |  | 2174.18 |  | 12 |  | 1.2 | 2.2 | 0 | 14.1 | 10
Group: "Ungrouped"
| 16_a |  |  | 16 | 1 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 0.2 |  | 0 | 0 | 0 | 0.2 | 10
| 33_a |  |  | 33 | 0.32 | 1.19 | 0.598 | 25 x 2,5 |  | UNIP_co | 1.902 |  | 2156.61 |  | 0.7 |  | 1.6 | 2.9 | 0.1 | 3.7 | 10
| 34 |  |  | 33_a | 0.32 | 0.97 | 0.533 | 25 x 2,5 |  | UNIP_co | 1.696 |  | 1760.59 |  | 0.6 |  | 3.2 | 4.6 | 0 | 5.2 | 10
| 35 |  |  | 34 | 7.62 | 0.77 | 0.466 | 25 x 2,5 |  | UNIP_co | 1.484 |  | 1391.88 |  | 10.6 |  | 4 | 4.4 | 0 | 15 | 10
| 36 |  |  | 35 | 0.81 | 0.3 | 0.3 | 18 x 2,0 |  | UNIP_co | 1.949 |  | 3496.44 |  | 2.8 |  | 4.4 | 8.4 | 0 | 11.2 | 10
| 37 |  |  | 35 | 1.31 | 0.47 | 0.346 | 20 x 2,25 |  | UNIP_co | 1.831 |  | 2762.49 |  | 3.6 |  | 0.8 | 1.3 | 0 | 5 | 10
| 38 |  |  | 37 | 1.24 | 0.21 | 0.198 | 16 x 2,0 |  | UNIP_co | 1.75 |  | 3500.85 |  | 4.3 |  | 3.6 | 5.5 | 0 | 9.8 | 10
| 39 |  |  | 38 | 1.36 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.71 |  | 0.8 |  | 6.8 | 1.3 | 0 | 2.1 | 10
| 40 |  |  | 38 | 0.78 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.72 |  | 0.4 |  | 2.4 | 0.5 | 0 | 0.9 | 10
| 41 |  |  | 38 | 2.63 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.69 |  | 1.5 |  | 6 | 1.1 | 0 | 2.6 | 10
| 42 |  |  | 37 | 1.31 | 0.26 | 0.232 | 18 x 2,0 |  | UNIP_co | 1.507 |  | 2223.19 |  | 2.9 |  | 2.4 | 2.7 | 0 | 5.6 | 10
| 43 |  |  | 42 | 0.49 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.73 |  | 0.8 |  | 4.2 | 2.8 | 0 | 3.6 | 10
| 44 |  |  | 42 | 1.18 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.71 |  | 2 |  | 1.4 | 0.9 | 0 | 2.9 | 10
| 45 |  |  | 34 | 0.77 | 0.2 | 0.191 | 16 x 2,0 |  | UNIP_co | 1.685 |  | 3276.17 |  | 2.5 |  | 2.2 | 3.1 | 0 | 5.6 | 10
| 46 |  |  | 45 | 0.61 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.8 |  | 0.3 |  | 5.2 | 1 | 0 | 1.3 | 10
| 47 |  |  | 45 | 1.58 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.91 |  | 2.6 |  | 5.6 | 3.7 | 0 | 6.3 | 10
| 47_a |  |  | 47 | 0.49 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.85 |  | 0.8 |  | 0 | 0 | 0 | 0.8 | 10
| 48 |  |  | 33_a | 2.87 | 0.22 | 0.205 | 16 x 2,0 |  | UNIP_co | 1.813 |  | 3726.74 |  | 10.7 |  | 4.8 | 7.9 | 0 | 18.6 | 10
| 49 |  |  | 48 | 0.53 | 0.15 | 0.15 | 16 x 2,0 |  | UNIP_co | 1.326 |  | 2151.52 |  | 1.1 |  | 5.2 | 4.6 | 0 | 5.7 | 10
| 50 |  |  | 48 | 2.38 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.74 |  | 1.3 |  | 1.6 | 0.3 | 0 | 1.7 | 10
Group: "Ungrouped"
| 7_d |  |  | 7_c | 0.37 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 0.1 |  | 0 | 0 | 0 | 0.1 | 10
| 8 |  |  | 7_d | 1.98 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 0.3 |  | 1.5 | 0.5 | 0 | 0.8 | 10
| 9 |  |  | 8 | 1.39 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 0.2 |  | 1.7 | 0.6 | 0 | 0.8 | 10
| 10 |  |  | 8 | 1.02 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 0.2 |  | 1.8 | 0.6 | 0 | 0.7 | 10
| 11 |  |  | 7_d | 10.71 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 1.6 |  | 1.5 | 0.5 | 0 | 2.1 | 10
| 12 |  |  | 11 | 0.09 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.32 |  | 0 |  | 1.7 | 0.6 | 0 | 0.6 | 10
| 13 |  |  | 11 | 4.25 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.32 |  | 0.6 |  | 1.8 | 0.6 | 0 | 1.2 | 10
| 18_a |  |  | 18 | 1.11 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.32 |  | 0.2 |  | 0 | 0 | 0 | 0.2 | 10
| 60_a |  |  | 60 | 4.55 | 0.35 | 0.285 | 18 x 2,0 |  | UNIP_co | 1.853 |  | 3198.48 |  | 14.5 |  | 0.4 | 0.7 | 0 | 15.2 | 10
| 61 |  |  | 60_a | 0.47 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.67 |  | 0.8 |  | 4.2 | 2.8 | 0 | 3.6 | 10
| 62 |  |  | 60_a | 2.72 | 0.22 | 0.205 | 16 x 2,0 |  | UNIP_co | 1.813 |  | 3726.07 |  | 10.1 |  | 1.8 | 3 | 0 | 13.1 | 10
| 63 |  |  | 62 | 1.29 | 0.15 | 0.15 | 16 x 2,0 |  | UNIP_co | 1.326 |  | 2151.1 |  | 2.8 |  | 5.2 | 4.6 | 0 | 7.4 | 10
| 64 |  |  | 62 | 1.52 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.65 |  | 0.9 |  | 1.6 | 0.3 | 0 | 1.2 | 10
Group: "Ungrouped"
| 10_b |  |  | 10_a | 1.01 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.32 |  | 0.2 |  | 0 | 0 | 0 | 0.2 | 10
| 12_b |  |  | 12_a | 0.93 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.32 |  | 0.1 |  | 0 | 0 | 0 | 0.1 | 10
| 19_a |  |  | 19 | 1.13 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.32 |  | 0.2 |  | 0 | 0 | 0 | 0.2 | 10
| 51_b |  |  | 51_a | 5.17 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.45 |  | 2.9 |  | 1.2 | 0.2 | 0 | 3.2 | 10
| 52_e |  |  | 52_d | 3.84 | 0.14 | 0.142 | 16 x 2,0 |  | UNIP_co | 1.251 |  | 1941.96 |  | 7.5 |  | 0.4 | 0.3 | 0 | 7.8 | 10
| 53 |  |  | 52_e | 0.95 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.37 |  | 0.5 |  | 5.2 | 1 | 0 | 1.5 | 10
| 54 |  |  | 52_e | 1.79 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.35 |  | 1 |  | 1.6 | 0.3 | 0 | 1.3 | 10
| 65_b |  |  | 65_a | 0.05 | 0.94 | 0.523 | 25 x 2,5 |  | UNIP_co | 1.666 |  | 1705.57 |  | 0.1 |  | 0 | 0 | 0 | 0.1 | 10
| 66 |  |  | 65_b | 2.1 | 0.87 | 0.501 | 25 x 2,5 |  | UNIP_co | 1.593 |  | 1577.09 |  | 3.3 |  | 3.2 | 4.1 | 0 | 7.4 | 10
| 67 |  |  | 66 | 0.28 | 0.2 | 0.191 | 16 x 2,0 |  | UNIP_co | 1.685 |  | 3275.55 |  | 0.9 |  | 3.2 | 4.5 | 0 | 5.5 | 10
| 68 |  |  | 67 | 0.59 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.63 |  | 1 |  | 5.2 | 3.4 | 0 | 4.4 | 10
| 69 |  |  | 67 | 1.65 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.67 |  | 0.9 |  | 1.6 | 0.3 | 0 | 1.2 | 10
| 70 |  |  | 66 | 0.9 | 0.67 | 0.43 | 25 x 2,5 |  | UNIP_co | 1.367 |  | 1203.91 |  | 1.1 |  | 0.8 | 0.7 | 0 | 1.8 | 10
| 71 |  |  | 70 | 0.28 | 0.2 | 0.191 | 16 x 2,0 |  | UNIP_co | 1.685 |  | 3275.51 |  | 0.9 |  | 3.2 | 4.5 | 0 | 5.5 | 10
| 72 |  |  | 71 | 0.59 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.61 |  | 1 |  | 5.2 | 3.4 | 0 | 4.4 | 10
| 73 |  |  | 71 | 1.65 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.66 |  | 0.9 |  | 1.6 | 0.3 | 0 | 1.2 | 10
| 74 |  |  | 70 | 0.91 | 0.47 | 0.346 | 20 x 2,25 |  | UNIP_co | 1.831 |  | 2762.2 |  | 2.5 |  | 0.8 | 1.3 | 0 | 3.8 | 10
| 75 |  |  | 74 | 0.28 | 0.2 | 0.191 | 16 x 2,0 |  | UNIP_co | 1.685 |  | 3275.47 |  | 0.9 |  | 3.6 | 5.1 | 0 | 6 | 10
| 76 |  |  | 75 | 0.6 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.59 |  | 1 |  | 5.2 | 3.4 | 0 | 4.4 | 10
| 77 |  |  | 75 | 1.64 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.66 |  | 0.9 |  | 1.6 | 0.3 | 0 | 1.2 | 10
| 78 |  |  | 74 | 0.35 | 0.27 | 0.238 | 18 x 2,0 |  | UNIP_co | 1.548 |  | 2331.51 |  | 0.8 |  | 2 | 2.4 | 0 | 3.2 | 10
| 79 |  |  | 78 | 1.22 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.66 |  | 0.7 |  | 4.2 | 0.8 | 0 | 1.5 | 10
| 80 |  |  | 78 | 0.73 | 0.2 | 0.191 | 16 x 2,0 |  | UNIP_co | 1.685 |  | 3275.43 |  | 2.4 |  | 1.4 | 2 | 0 | 4.4 | 10
| 81 |  |  | 80 | 0.5 | 0.13 | 0.13 | 16 x 2,0 |  | UNIP_co | 1.149 |  | 1673.56 |  | 0.8 |  | 5.2 | 3.4 | 0 | 4.3 | 10
| 82 |  |  | 80 | 1.75 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.64 |  | 1 |  | 1.6 | 0.3 | 0 | 1.3 | 10
| 83 |  |  | 65_b | 3.55 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.65 |  | 2 |  | 3 | 0.6 | 0 | 2.6 | 10
| 101_d |  |  | 101_c | 3.91 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.04 |  | 2.2 |  | 1.2 | 0.2 | 0 | 2.4 | 10
Group: "Ungrouped"
| 7_a |  |  | 7 | 0.23 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.34 |  | 0 |  | 1.4 | 0.5 | 0 | 0.5 | 10
| 7_b |  |  | 7_a | 5.22 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.34 |  | 0.8 |  | 1.4 | 0.5 | 0 | 1.3 | 10
| 7_c |  |  | 7_b | 0.24 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 0 |  | 0 | 0 | 0 | 0 | 10
| 10_a |  |  | 10 | 3.25 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 0.5 |  | 2.8 | 0.9 | 0 | 1.4 | 10
| 12_a |  |  | 12 | 3.39 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.32 |  | 0.5 |  | 2.8 | 0.9 | 0 | 1.4 | 10
| 15_a |  |  | 15 | 0.2 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 0 |  | 1.4 | 0.5 | 0 | 0.5 | 10
| 15_b |  |  | 15_a | 1.42 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 0.2 |  | 0 | 0 | 0 | 0.2 | 10
| 16 |  |  | 15_b | 0.2 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 0 |  | 1.7 | 0.6 | 0 | 0.6 | 10
| 17 |  |  | 15_b | 3.78 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.33 |  | 0.6 |  | 0.4 | 0.1 | 0 | 0.7 | 10
| 18 |  |  | 17 | 0.28 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.32 |  | 0 |  | 1.7 | 0.6 | 0 | 0.6 | 10
| 19 |  |  | 17 | 3.28 | 0 | 1.66 | 63 x 6,0 |  | UNIP_le | 0.813 |  | 151.32 |  | 0.5 |  | 1.8 | 0.6 | 0 | 1.1 | 10
| 24_a |  |  | 24 | 11.3 | 1.2 | 0.6 | 25 x 2,5 |  | UNIP_co | 1.911 |  | 2174.29 |  | 24.6 |  | 0.8 | 1.5 | 0 | 26 | 10
| 32_a |  |  | 32 | 0.32 | 1.26 | 0.617 | 25 x 2,5 |  | UNIP_co | 1.963 |  | 2280.82 |  | 0.7 |  | 2.8 | 5.4 | 0 | 6.1 | 10
| 32_b |  |  | 32_a | 1.45 | 1.26 | 0.617 | 25 x 2,5 |  | UNIP_co | 1.963 |  | 2280.8 |  | 3.3 |  | 0 | 0 | 0 | 3.3 | 10
| 33 |  |  | 32_b | 0.31 | 1.19 | 0.598 | 25 x 2,5 |  | UNIP_co | 1.902 |  | 2156.62 |  | 0.7 |  | 3.2 | 5.8 | 0 | 6.4 | 10
| 51 |  |  | 32_b | 7.05 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.7 |  | 4 |  | 6.2 | 1.2 | 0 | 5.2 | 10
| 51_a |  |  | 51 | 0.36 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.56 |  | 0.2 |  | 0 | 0 | 0 | 0.2 | 10
| 52_b |  |  | 52_a | 0.41 | 0.14 | 0.142 | 20 x 2,25 |  | UNIP_co | 0.75 |  | 575.74 |  | 0.2 |  | 5.6 | 1.6 | 0 | 1.8 | 10
| 52_c |  |  | 52_b | 8.53 | 0.14 | 0.142 | 16 x 2,0 |  | UNIP_co | 1.251 |  | 1942.6 |  | 16.6 |  | 4.4 | 3.4 | 0 | 20 | 10
| 52_d |  |  | 52_c | 0.51 | 0.14 | 0.142 | 16 x 2,0 |  | UNIP_co | 1.251 |  | 1942.09 |  | 1 |  | 0 | 0 | 0 | 1 | 10
| 59_a |  |  | 59 | 0.51 | 1.29 | 0.625 | 25 x 2,5 |  | UNIP_co | 1.989 |  | 2333.69 |  | 1.2 |  | 2.8 | 5.5 | 0 | 6.7 | 10
| 59_b |  |  | 59_a | 5.29 | 1.29 | 0.625 | 25 x 2,5 |  | UNIP_co | 1.989 |  | 2333.59 |  | 12.4 |  | 0 | 0 | 0 | 12.4 | 10
| 60 |  |  | 59_b | 0.5 | 0.35 | 0.285 | 18 x 2,0 |  | UNIP_co | 1.853 |  | 3198.61 |  | 1.6 |  | 3.2 | 5.5 | 0 | 7.1 | 10
| 65 |  |  | 59_b | 3.29 | 0.94 | 0.523 | 25 x 2,5 |  | UNIP_co | 1.666 |  | 1705.63 |  | 5.6 |  | 3.6 | 5 | 0 | 10.6 | 10
| 65_a |  |  | 65 | 0.55 | 0.94 | 0.523 | 25 x 2,5 |  | UNIP_co | 1.666 |  | 1705.57 |  | 0.9 |  | 0 | 0 | 0 | 0.9 | 10
| 101_a |  |  | 101 | 0.43 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.46 |  | 0.2 |  | 4.4 | 0.8 | 0 | 1.1 | 10
| 101_b |  |  | 101_a | 8.66 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.29 |  | 4.9 |  | 4.4 | 0.8 | 0 | 5.7 | 10
| 101_c |  |  | 101_b | 0.58 | 0.07 | 0.07 | 16 x 2,0 |  | UNIP_co | 0.619 |  | 566.12 |  | 0.3 |  | 0 | 0 | 0 | 0.3 | 10
| 102_a |  |  | 102 | 11.26 | 1.2 | 0.6 | 25 x 2,5 |  | UNIP_co | 1.911 |  | 2173.93 |  | 24.5 |  | 0.8 | 1.5 | 0 | 25.9 | 10
Group: "Ungrouped"
| 24_b |  |  | 24_a | 0.94 | 1.2 | 0.6 | 25 x 2,5 |  | UNIP_co | 1.911 |  | 2174.06 |  | 2.1 |  | 0.4 | 0.7 | 0 | 2.8 | 10
| 25 |  |  | 24_b | 0.56 | 0.3 | 0.3 | 18 x 2,0 |  | UNIP_co | 1.949 |  | 3496.23 |  | 1.9 |  | 3.2 | 6.1 | 0 | 8 | 10
| 26 |  |  | 24_b | 0.12 | 0.9 | 0.51 | 25 x 2,5 |  | UNIP_co | 1.625 |  | 1632.3 |  | 0.2 |  | 0.8 | 1.1 | 0 | 1.3 | 10
| 27 |  |  | 26 | 0.57 | 0.3 | 0.3 | 18 x 2,0 |  | UNIP_co | 1.949 |  | 3496.22 |  | 2 |  | 3.2 | 6.1 | 0 | 8.1 | 10
| 28 |  |  | 26 | 4.14 | 0.6 | 0.402 | 25 x 2,5 |  | UNIP_co | 1.279 |  | 1070.98 |  | 4.4 |  | 0.8 | 0.7 | 0 | 5.1 | 10
| 29 |  |  | 28 | 0.61 | 0.3 | 0.3 | 18 x 2,0 |  | UNIP_co | 1.949 |  | 3496.01 |  | 2.1 |  | 3.2 | 6.1 | 0 | 8.2 | 10
| 30 |  |  | 28 | 0.73 | 0.3 | 0.3 | 18 x 2,0 |  | UNIP_co | 1.949 |  | 3496.01 |  | 2.5 |  | 1.2 | 2.3 | 0 | 4.8 | 10
| 102_b |  |  | 102_a | 3.58 | 1.2 | 0.6 | 25 x 2,5 |  | UNIP_co | 1.911 |  | 2173.68 |  | 7.8 |  | 0.4 | 0.7 | 0 | 8.5 | 10
| 103 |  |  | 102_b | 0.5 | 0.3 | 0.3 | 18 x 2,0 |  | UNIP_co | 1.949 |  | 3495.55 |  | 1.7 |  | 3.2 | 6.1 | 0 | 7.8 | 10
| 104 |  |  | 102_b | 0.17 | 0.9 | 0.51 | 25 x 2,5 |  | UNIP_co | 1.625 |  | 1631.99 |  | 0.3 |  | 0.8 | 1.1 | 0 | 1.3 | 10
| 105 |  |  | 104 | 0.5 | 0.3 | 0.3 | 18 x 2,0 |  | UNIP_co | 1.949 |  | 3495.55 |  | 1.8 |  | 3.2 | 6.1 | 0 | 7.8 | 10
| 106 |  |  | 104 | 3.6 | 0.6 | 0.402 | 25 x 2,5 |  | UNIP_co | 1.279 |  | 1070.78 |  | 3.9 |  | 0.8 | 0.7 | 0 | 4.5 | 10
| 107 |  |  | 106 | 0.55 | 0.3 | 0.3 | 18 x 2,0 |  | UNIP_co | 1.949 |  | 3495.36 |  | 1.9 |  | 3.2 | 6.1 | 0 | 8 | 10
| 108 |  |  | 106 | 0.68 | 0.3 | 0.3 | 18 x 2,0 |  | UNIP_co | 1.949 |  | 3495.36 |  | 2.4 |  | 1.2 | 2.3 | 0 | 4.6 | 10

## Hot water pipe-runs
| ## |  |  | CPRNo. |  | L [m] | ΣVr [dm³/s] |  | Vs [dm³/s] | Diameter |  |  | Piperun type |  | v [m/s] |  | R [Pa/m] |  |  | R*L [kPa] |  |  | Σζ | Z [kPa] |  | Δparm [kPa] | Δp [kPa] | Insul. [mm]
Group: "Ungrouped"
| H57 |  |  |  |  | 4.26 | 1.48 |  | 0.674 | 32 x 3,0 |  |  | UNIP_co |  | 1.269 |  | 589.55 |  |  | 2.5 |  |  | 7.4 | 6 |  | 0 | 8.5 | 40
|  | Valve: | Shutoff valve, incl. | [7 empty] | Diameter: | 25 |  |  | Δp= | 1.7 |  |  | [kPa] |  |  | Setting:
| H57_a |  |  | H57 |  | 3.36 | 1.48 |  | 0.674 | 32 x 3,0 |  |  | UNIP_co |  | 1.269 |  | 589.58 |  |  | 2 |  |  | 0 | 0 |  | 0 | 2 | 40
| H58 |  |  | H57_a |  | 4.47 | 0.56 |  | 0.385 | 25 x 2,5 |  |  | UNIP_co |  | 1.227 |  | 764.59 |  |  | 3.4 |  |  | 2.6 | 1.9 |  | 0 | 5.3 | 25
| H58_a |  |  | H58 |  | 5.7 | 0.56 |  | 0.385 | 25 x 2,5 |  |  | UNIP_co |  | 1.227 |  | 764.68 |  |  | 4.4 |  |  | 0 | 0 |  | 0 | 4.4 | 25
| H59 |  |  | H58_a |  | 0.26 | 0.42 |  | 0.322 | 20 x 2,25 |  |  | UNIP_co |  | 1.704 |  | 1873.78 |  |  | 0.5 |  |  | 3.2 | 4.6 |  | 0 | 5.1 | 25
| H70 |  |  | H58_a |  | 1.36 | 0.14 |  | 0.142 | 20 x 2,25 |  |  | UNIP_co |  | 0.75 |  | 437.45 |  |  | 0.6 |  |  | 3.8 | 1.1 |  | 0 | 1.6 | 25
| H70_a |  |  | H70 |  | 5.38 | 0.14 |  | 0.142 | 20 x 2,25 |  |  | UNIP_co |  | 0.75 |  | 437.53 |  |  | 2.4 |  |  | 0 | 0 |  | 0 | 2.4 | 25
| H74 |  |  | H57_a |  | 15.12 | 0.92 |  | 0.517 | 25 x 2,5 |  |  | UNIP_co |  | 1.645 |  | 1289.89 |  |  | 19.5 |  |  | 3.9 | 5.2 |  | 0 | 24.7 | 25
| H74_a |  |  | H74 |  | 5.77 | 0.92 |  | 0.517 | 25 x 2,5 |  |  | UNIP_co |  | 1.645 |  | 1290.12 |  |  | 7.4 |  |  | 0 | 0 |  | 0 | 7.4 | 25
| H75 |  |  | H74_a |  | 2.31 | 0.64 |  | 0.418 | 25 x 2,5 |  |  | UNIP_co |  | 1.33 |  | 883.48 |  |  | 2 |  |  | 3.2 | 2.8 |  | 0 | 4.8 | 25
| H91 |  |  | H74_a |  | 1.84 | 0.28 |  | 0.245 | 20 x 2,25 |  |  | UNIP_co |  | 1.296 |  | 1152.33 |  |  | 2.1 |  |  | 1.8 | 1.5 |  | 0 | 3.6 | 25
| H92 |  |  | H91 |  | 4.63 | 0.21 |  | 0.198 | 16 x 2,0 |  |  | UNIP_co |  | 1.75 |  | 2685.62 |  |  | 12.4 |  |  | 3.6 | 5.4 |  | 0 | 17.8 | 25
| H93 |  |  | H92 |  | 1.1 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428 |  |  | 0.5 |  |  | 5.6 | 1.1 |  | 0 | 1.5 | 25
| H94 |  |  | H92 |  | 6.77 | 0.14 |  | 0.142 | 16 x 2,0 |  |  | UNIP_co |  | 1.251 |  | 1482.84 |  |  | 10 |  |  | 6 | 4.6 |  | 0 | 14.7 | 25
| H94_a |  |  | H94 |  | 0.28 | 0.14 |  | 0.142 | 16 x 2,0 |  |  | UNIP_co |  | 1.251 |  | 1483.07 |  |  | 0.4 |  |  | 0 | 0 |  | 0 | 0.4 | 25
| H95 |  |  | H94_a |  | 0.73 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.13 |  |  | 0.3 |  |  | 4.6 | 0.9 |  | 0 | 1.2 | 25
| H96 |  |  | H94_a |  | 0.9 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.14 |  |  | 0.4 |  |  | 4.6 | 0.9 |  | 0 | 1.3 | 25
| H97 |  |  | H91 |  | 15.94 | 0.07 |  | 0.066 | 20 x 2,25 |  |  | UNIP_co |  | 0.35 |  | 114.63 |  |  | 1.8 |  |  | 3.8 | 0.2 |  | 0 | 2.1 | 25
| H97_a |  |  | H97 |  | 7.93 | 0.07 |  | 0.066 | 20 x 2,25 |  |  | UNIP_co |  | 0.35 |  | 114.8 |  |  | 0.9 |  |  | 0.4 | 0 |  | 0 | 0.9 | 25
| Heater |  |  |  | CPRNo. |  |  | ΣVr [dm³/s] |  |  | Vs [dm³/s] | Press. drop [kPa] |  | Circ.pr.drop [kPa] |  |  |  | VsCirc [dm³/s] |  |  | Circ. pump press. [kPa] |  |  |  | Circ.Temp [°C]
| Speicher TWE |  |  |  | 56 |  |  | 1.48 |  |  | 0.674 | 1.2 |  | 0 |  |  |  | 0.09 |  |  | - |  |  |  | 55.9
Group: "Ungrouped"
| H60_a |  |  | H60 |  | 0.42 | 0.35 |  | 0.285 | 18 x 2,0 |  |  | UNIP_co |  | 1.853 |  | 2462.01 |  |  | 1 |  |  | 0 | 0 |  | 0 | 1 | 25
| H61 |  |  | H60_a |  | 0.32 | 0.28 |  | 0.245 | 18 x 2,0 |  |  | UNIP_co |  | 1.589 |  | 1873.46 |  |  | 0.6 |  |  | 3.7 | 4.6 |  | 0 | 5.2 | 25
| H62 |  |  | H61 |  | 9.95 | 0.21 |  | 0.198 | 16 x 2,0 |  |  | UNIP_co |  | 1.75 |  | 2685.54 |  |  | 26.7 |  |  | 5.4 | 8.1 |  | 0 | 34.9 | 25
| H63 |  |  | H62 |  | 1.06 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.03 |  |  | 0.5 |  |  | 6.8 | 1.3 |  | 0 | 1.7 | 25
| H64 |  |  | H62 |  | 0.59 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.02 |  |  | 0.3 |  |  | 2.4 | 0.5 |  | 0 | 0.7 | 25
| H65 |  |  | H62 |  | 2.78 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.06 |  |  | 1.2 |  |  | 6 | 1.1 |  | 0 | 2.3 | 25
| H66 |  |  | H61 |  | 0.97 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 427.88 |  |  | 0.4 |  |  | 5.8 | 1.1 |  | 0 | 1.5 | 25
| H66_a |  |  | H66 |  | 0.71 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 427.92 |  |  | 0.3 |  |  | 0 | 0 |  | 0 | 0.3 | 25
| H67 |  |  | H60_a |  | 5.1 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 427.96 |  |  | 2.2 |  |  | 4.5 | 0.8 |  | 0 | 3 | 25
Group: "Ungrouped"
| H76_a |  |  | H76 |  | 6.91 | 0.22 |  | 0.205 | 16 x 2,0 |  |  | UNIP_co |  | 1.813 |  | 2860.68 |  |  | 19.8 |  |  | 1.2 | 1.9 |  | 0 | 21.7 | 25
| H77 |  |  | H76_a |  | 1.39 | 0.15 |  | 0.15 | 16 x 2,0 |  |  | UNIP_co |  | 1.326 |  | 1643.41 |  |  | 2.3 |  |  | 5.2 | 4.5 |  | 0 | 6.8 | 25
| H78 |  |  | H76_a |  | 1.67 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.09 |  |  | 0.7 |  |  | 1.6 | 0.3 |  | 0 | 1 | 25
Group: "Ungrouped"
| H69_a |  |  | H69 |  | 4.92 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.19 |  |  | 2.1 |  |  | 1.2 | 0.2 |  | 0 | 2.3 | 25
| H71_a |  |  | H71 |  | 3.49 | 0.14 |  | 0.142 | 16 x 2,0 |  |  | UNIP_co |  | 1.251 |  | 1483.31 |  |  | 5.2 |  |  | 0.4 | 0.3 |  | 0 | 5.5 | 25
| H72 |  |  | H71_a |  | 1.05 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.24 |  |  | 0.4 |  |  | 5.2 | 1 |  | 0 | 1.4 | 25
| H73 |  |  | H71_a |  | 1.89 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.26 |  |  | 0.8 |  |  | 1.6 | 0.3 |  | 0 | 1.1 | 25
| H80_a |  |  | H80 |  | 0.15 | 0.42 |  | 0.322 | 20 x 2,25 |  |  | UNIP_co |  | 1.704 |  | 1874.38 |  |  | 0.3 |  |  | 0 | 0 |  | 0 | 0.3 | 25
| H81 |  |  | H80_a |  | 2.1 | 0.35 |  | 0.285 | 18 x 2,0 |  |  | UNIP_co |  | 1.853 |  | 2462.73 |  |  | 5.2 |  |  | 3.6 | 6.1 |  | 0 | 11.2 | 25
| H82 |  |  | H81 |  | 2.23 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.05 |  |  | 1 |  |  | 4.6 | 0.9 |  | 0 | 1.8 | 25
| H83 |  |  | H81 |  | 0.9 | 0.28 |  | 0.245 | 18 x 2,0 |  |  | UNIP_co |  | 1.589 |  | 1874.07 |  |  | 1.7 |  |  | 1 | 1.2 |  | 0 | 2.9 | 25
| H84 |  |  | H83 |  | 2.23 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.06 |  |  | 1 |  |  | 4.6 | 0.9 |  | 0 | 1.8 | 25
| H85 |  |  | H83 |  | 0.91 | 0.21 |  | 0.198 | 16 x 2,0 |  |  | UNIP_co |  | 1.75 |  | 2686.06 |  |  | 2.4 |  |  | 1 | 1.5 |  | 0 | 3.9 | 25
| H86 |  |  | H85 |  | 2.22 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.07 |  |  | 1 |  |  | 5.6 | 1.1 |  | 0 | 2 | 25
| H87 |  |  | H85 |  | 0.3 | 0.14 |  | 0.142 | 16 x 2,0 |  |  | UNIP_co |  | 1.251 |  | 1482.79 |  |  | 0.4 |  |  | 1.2 | 0.9 |  | 0 | 1.4 | 25
| H88 |  |  | H87 |  | 1.12 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.06 |  |  | 0.5 |  |  | 5.2 | 1 |  | 0 | 1.5 | 25
| H89 |  |  | H87 |  | 2.83 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.09 |  |  | 1.2 |  |  | 2 | 0.4 |  | 0 | 1.6 | 25
| H90 |  |  | H80_a |  | 3.4 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.05 |  |  | 1.5 |  |  | 3.4 | 0.6 |  | 0 | 2.1 | 25
| H98_a |  |  | H98 |  | 4.16 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 429.61 |  |  | 1.8 |  |  | 1.2 | 0.2 |  | 0 | 2 | 25
Group: "Ungrouped"
| H59_a |  |  | H59 |  | 0.42 | 0.42 |  | 0.322 | 20 x 2,25 |  |  | UNIP_co |  | 1.704 |  | 1873.8 |  |  | 0.8 |  |  | 3 | 4.3 |  | 0 | 5.1 | 25
| H59_b |  |  | H59_a |  | 1.46 | 0.42 |  | 0.322 | 20 x 2,25 |  |  | UNIP_co |  | 1.704 |  | 1873.83 |  |  | 2.7 |  |  | 0 | 0 |  | 0 | 2.7 | 25
| H60 |  |  | H59_b |  | 0.41 | 0.35 |  | 0.285 | 18 x 2,0 |  |  | UNIP_co |  | 1.853 |  | 2461.98 |  |  | 1 |  |  | 3.6 | 6.1 |  | 0 | 7.1 | 25
| H68 |  |  | H59_b |  | 7.05 | 0.07 |  | 0.066 | 16 x 2,0 |  |  | UNIP_co |  | 0.584 |  | 386.91 |  |  | 2.7 |  |  | 3.4 | 0.6 |  | 0 | 3.3 | 25
| H69 |  |  | H68 |  | 0.46 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 428.08 |  |  | 0.2 |  |  | 0 | 0 |  | 0 | 0.2 | 25
| H70_b |  |  | H70_a |  | 0.51 | 0.14 |  | 0.142 | 20 x 2,25 |  |  | UNIP_co |  | 0.75 |  | 437.61 |  |  | 0.2 |  |  | 5.6 | 1.5 |  | 0 | 1.8 | 25
| H70_c |  |  | H70_b |  | 8.53 | 0.14 |  | 0.142 | 16 x 2,0 |  |  | UNIP_co |  | 1.251 |  | 1482.95 |  |  | 12.6 |  |  | 1.2 | 0.9 |  | 0 | 13.6 | 25
| H71 |  |  | H70_c |  | 0.61 | 0.14 |  | 0.142 | 16 x 2,0 |  |  | UNIP_co |  | 1.251 |  | 1483.17 |  |  | 0.9 |  |  | 0 | 0 |  | 0 | 0.9 | 25
| H75_a |  |  | H75 |  | 0.61 | 0.64 |  | 0.418 | 25 x 2,5 |  |  | UNIP_co |  | 1.33 |  | 883.51 |  |  | 0.5 |  |  | 2.8 | 2.4 |  | 0 | 3 | 25
| H75_b |  |  | H75_a |  | 5.29 | 0.64 |  | 0.418 | 25 x 2,5 |  |  | UNIP_co |  | 1.33 |  | 883.55 |  |  | 4.7 |  |  | 0 | 0 |  | 0 | 4.7 | 25
| H76 |  |  | H75_b |  | 0.6 | 0.22 |  | 0.205 | 16 x 2,0 |  |  | UNIP_co |  | 1.813 |  | 2860.36 |  |  | 1.7 |  |  | 3.2 | 5.2 |  | 0 | 6.9 | 25
| H79 |  |  | H75_b |  | 3.29 | 0.42 |  | 0.322 | 20 x 2,25 |  |  | UNIP_co |  | 1.704 |  | 1874.31 |  |  | 6.2 |  |  | 1.6 | 2.3 |  | 0 | 8.4 | 25
| H80 |  |  | H79 |  | 0.65 | 0.42 |  | 0.322 | 20 x 2,25 |  |  | UNIP_co |  | 1.704 |  | 1874.37 |  |  | 1.2 |  |  | 0 | 0 |  | 0 | 1.2 | 25
| H97_b |  |  | H97_a |  | 0.53 | 0.07 |  | 0.066 | 20 x 2,25 |  |  | UNIP_co |  | 0.35 |  | 114.86 |  |  | 0.1 |  |  | 5.6 | 0.3 |  | 0 | 0.4 | 25
| H97_c |  |  | H97_b |  | 8.66 | 0.07 |  | 0.066 | 16 x 2,0 |  |  | UNIP_co |  | 0.584 |  | 388.18 |  |  | 3.4 |  |  | 1.2 | 0.2 |  | 0 | 3.6 | 25
| H98 |  |  | H97_c |  | 0.68 | 0.07 |  | 0.07 | 16 x 2,0 |  |  | UNIP_co |  | 0.619 |  | 429.51 |  |  | 0.3 |  |  | 0 | 0 |  | 0 | 0.3 | 25
Group: "Ungrouped"

## Circulation pipe-runs
|  |  | CPRNo. |  |  | Type | L [m] | VsCirc [dm³/s] | Diameter |  | Piperun type |  |  |  | vCirc [m/s] | RCirc [Pa/m] |  |  |  |  | Σζ |  | ZCirc [kPa] |  | Δparm [kPa] |  | Δp [kPa] | Δθ [K] | Insul. [mm]
Group: "Ungrouped"
| H57 |  |  |  |  | Circ | 3.88 | 0.09 | 20 x 2,25 |  | UNIP_co |  |  |  | 0.48 | 202.02 |  |  |  |  | 15.3 |  | 1.83 |  | -12.11 |  | -9.49 | 0.08 | 25
|  | Valve: |  | Shutoff valve, incl. | [5 empty] | Diameter: |  |  | 15 |  |  |  | Δp= |  |  | 0.9 |  |  |  | [kPa] |  | Setting:
|  | Valve: |  | Shutoff valve with NR va | [5 empty] | Diameter: |  |  | 20 |  |  |  | Δp= |  |  | 0.3 |  |  |  | [kPa] |  | Setting:
|  | Pump: |  |  | no name | [5 empty] | Vs= | 0.09 |  | [dm³/s] |  |  |  | H= | 12.1 |  |  | [kPa]
| H57_a |  | H57 |  |  | Circ | 3.64 | 0.09 | 20 x 2,25 |  | UNIP_co |  |  |  | 0.48 | 201.96 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0.73 | 0.07 | 25
| H58 |  | H57_a |  |  | Circ | 10.38 | 0.045 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.4 | 200.71 |  |  |  |  | 3.6 |  | 0.28 |  | 0 |  | 2.37 | 0.39 | 25
| H59 |  | H58 |  |  | Circ | 0.36 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.54 |  |  |  |  | 5.2 |  | 0.1 |  | 0 |  | 0.12 | 0.03 | 25
| H60 |  | H58 |  |  | Circ | 1.16 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.8 |  |  |  |  | 5.6 |  | 0.11 |  | 0 |  | 0.18 | 0.09 | 25
| H60_a |  | H60 |  |  | Circ | 5.28 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.74 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0.32 | 0.4 | 25
| H61 |  | H57_a |  |  | Circ | 15.12 | 0.045 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.4 | 202.86 |  |  |  |  | 5.6 |  | 0.44 |  | 0 |  | 3.51 | 0.54 | 25
| H61_a |  | H61 |  |  | Circ | 5.77 | 0.045 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.4 | 202.53 |  |  |  |  | 0 |  | 0 |  | 0 |  | 1.17 | 0.21 | 25
| H62 |  | H61_a |  |  | Circ | 2.41 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.78 |  |  |  |  | 5.2 |  | 0.1 |  | 0 |  | 0.25 | 0.18 | 25
| H63 |  | H61_a |  |  | Circ | 17.78 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 60.55 |  |  |  |  | 5.6 |  | 0.11 |  | 0 |  | 1.19 | 1.25 | 25
| H63_a |  | H63 |  |  | Circ | 7.83 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 60.31 |  |  |  |  | 0.4 |  | 0.01 |  | 0 |  | 0.48 | 0.57 | 25
| H57 |  |  |  |  | HW | 4.26 | 0.09 | 32 x 3,0 |  | UNIP_co |  |  |  | 0.17 | 16.98 |  |  |  |  | 7.4 |  | 0.08 |  | 0 |  | 0.15 | 0.1 | 40
|  | Valve: |  | Shutoff valve, incl. | [5 empty] | Diameter: |  |  | 25 |  |  |  | Δp= |  |  | 1.7 |  |  |  | [kPa] |  | Setting:
| H57_a |  | H57 |  |  | HW | 3.36 | 0.09 | 32 x 3,0 |  | UNIP_co |  |  |  | 0.17 | 16.99 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0.06 | 0.08 | 40
| H58 |  | H57_a |  |  | HW | 4.47 | 0.045 | 25 x 2,5 |  | UNIP_co |  |  |  | 0.144 | 17.57 |  |  |  |  | 2.6 |  | 0.03 |  | 0 |  | 0.11 | 0.23 | 25
| H58_a |  | H58 |  |  | HW | 5.7 | 0.045 | 25 x 2,5 |  | UNIP_co |  |  |  | 0.144 | 17.59 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0.1 | 0.29 | 25
| H59 |  | H58_a |  |  | HW | 0.26 | 0.023 | 20 x 2,25 |  | UNIP_co |  |  |  | 0.12 | 17.61 |  |  |  |  | 3.2 |  | 0.02 |  | 0 |  | 0.03 | 0.02 | 25
| H70 |  | H58_a |  |  | HW | 1.36 | 0.023 | 20 x 2,25 |  | UNIP_co |  |  |  | 0.12 | 17.61 |  |  |  |  | 3.8 |  | 0.03 |  | 0 |  | 0.05 | 0.12 | 25
| H70_a |  | H70 |  |  | HW | 5.38 | 0.023 | 20 x 2,25 |  | UNIP_co |  |  |  | 0.12 | 17.63 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0.09 | 0.48 | 25
| H74 |  | H57_a |  |  | HW | 15.12 | 0.045 | 25 x 2,5 |  | UNIP_co |  |  |  | 0.144 | 17.59 |  |  |  |  | 3.9 |  | 0.04 |  | 0 |  | 0.31 | 0.78 | 25
| H74_a |  | H74 |  |  | HW | 5.77 | 0.045 | 25 x 2,5 |  | UNIP_co |  |  |  | 0.144 | 17.63 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0.1 | 0.29 | 25
| H75 |  | H74_a |  |  | HW | 2.31 | 0.023 | 25 x 2,5 |  | UNIP_co |  |  |  | 0.072 | 5.27 |  |  |  |  | 3.2 |  | 0.01 |  | 0 |  | 0.02 | 0.23 | 25
| H91 |  | H74_a |  |  | HW | 1.84 | 0.023 | 20 x 2,25 |  | UNIP_co |  |  |  | 0.12 | 17.65 |  |  |  |  | 1.8 |  | 0.01 |  | 0 |  | 0.05 | 0.16 | 25
| H97 |  | H91 |  |  | HW | 15.94 | 0.023 | 20 x 2,25 |  | UNIP_co |  |  |  | 0.12 | 17.71 |  |  |  |  | 3.8 |  | 0.03 |  | 0 |  | 0.31 | 1.4 | 25
| H97_a |  | H97 |  |  | HW | 7.93 | 0.023 | 20 x 2,25 |  | UNIP_co |  |  |  | 0.12 | 17.79 |  |  |  |  | 0.4 |  | 0 |  | 0 |  | 0.14 | 0.68 | 25
Group: "Ungrouped"
Group: "Ungrouped"
Group: "Ungrouped"
Group: "Ungrouped"
| H59_a |  | H59 |  |  | Circ | 0.52 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.53 |  |  |  |  | 4.4 |  | 0.09 |  | 0 |  | 0.12 | 0.05 | 25
| H59_b |  | H59_a |  |  | Circ | 8.6 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.47 |  |  |  |  | 4.4 |  | 0.09 |  | 0 |  | 0.6 | 0.44 | 25
| H59_c |  | H59_b |  |  | Circ | 0.1 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.41 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0.01 | 0.01 | 25
| H60_b |  | H60_a |  |  | Circ | 0.61 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.68 |  |  |  |  | 4.4 |  | 0.09 |  | 0 |  | 0.12 | 0.06 | 25
| H60_c |  | H60_b |  |  | Circ | 8.63 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.61 |  |  |  |  | 4.4 |  | 0.09 |  | 0 |  | 0.6 | 0.43 | 25
| H60_d |  | H60_c |  |  | Circ | 0.1 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.56 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0.01 | 0.01 | 25
| H62_a |  | H62 |  |  | Circ | 0.71 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.75 |  |  |  |  | 4.4 |  | 0.09 |  | 0 |  | 0.13 | 0.07 | 25
| H62_b |  | H62_a |  |  | Circ | 8.68 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.69 |  |  |  |  | 4.4 |  | 0.09 |  | 0 |  | 0.6 | 0.43 | 25
| H62_c |  | H62_b |  |  | Circ | 0.1 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.63 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0.01 | 0.01 | 25
| H63_b |  | H63_a |  |  | Circ | 0.63 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 60.23 |  |  |  |  | 4.4 |  | 0.09 |  | 0 |  | 0.12 | 0.06 | 25
| H63_c |  | H63_b |  |  | Circ | 8.76 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 60.17 |  |  |  |  | 4.4 |  | 0.09 |  | 0 |  | 0.61 | 0.4 | 25
| H63_d |  | H63_c |  |  | Circ | 0.1 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 60.11 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0.01 | 0.01 | 25
| H59_a |  | H59 |  |  | HW | 0.42 | 0.023 | 20 x 2,25 |  | UNIP_co |  |  |  | 0.12 | 17.61 |  |  |  |  | 3 |  | 0.02 |  | 0 |  | 0.03 | 0.05 | 25
| H59_b |  | H59_a |  |  | HW | 1.46 | 0.023 | 20 x 2,25 |  | UNIP_co |  |  |  | 0.12 | 17.62 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0.03 | 0.09 | 25
| H68 |  | H59_b |  |  | HW | 7.05 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.36 |  |  |  |  | 3.4 |  | 0.07 |  | 0 |  | 0.49 | 0.37 | 25
| H70_b |  | H70_a |  |  | HW | 0.51 | 0.023 | 20 x 2,25 |  | UNIP_co |  |  |  | 0.12 | 17.65 |  |  |  |  | 5.6 |  | 0.04 |  | 0 |  | 0.05 | 0.06 | 25
| H70_c |  | H70_b |  |  | HW | 8.53 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 59.5 |  |  |  |  | 1.2 |  | 0.02 |  | 0 |  | 0.53 | 0.44 | 25
| H75_a |  | H75 |  |  | HW | 0.61 | 0.023 | 25 x 2,5 |  | UNIP_co |  |  |  | 0.072 | 5.28 |  |  |  |  | 2.8 |  | 0.01 |  | 0 |  | 0.01 | 0.08 | 25
| H75_b |  | H75_a |  |  | HW | 5.29 | 0.023 | 25 x 2,5 |  | UNIP_co |  |  |  | 0.072 | 5.28 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0.03 | 0.34 | 25
| H79 |  | H75_b |  |  | HW | 3.29 | 0.023 | 20 x 2,25 |  | UNIP_co |  |  |  | 0.12 | 17.7 |  |  |  |  | 1.6 |  | 0.01 |  | 0 |  | 0.07 | 0.19 | 25
| H97_b |  | H97_a |  |  | HW | 0.53 | 0.023 | 20 x 2,25 |  | UNIP_co |  |  |  | 0.12 | 17.82 |  |  |  |  | 5.6 |  | 0.04 |  | 0 |  | 0.05 | 0.06 | 25
| H97_c |  | H97_b |  |  | HW | 8.66 | 0.023 | 16 x 2,0 |  | UNIP_co |  |  |  | 0.2 | 60.06 |  |  |  |  | 1.2 |  | 0.02 |  | 0 |  | 0.54 | 0.41 | 25
Group: "Ungrouped"

## List of pipes, pipe fittings an
B. MATERJALIDE JA SEADMETE SPETSIFIKATSIOON
(siseveevarustus)
|  | Toode | Mõõt | Kataloogi kood | Kogus | Ühik
San. seadmed
|  | valamu kangsegisti ja sifooniga (ruum nr. 301, 302, 309, 310, 312) | 661x415 mm |  | 6 | tk.
|  | fajanss kätepesuvalamu kangsegisti ja sifooniga (ruum nr. 305-308) | 400x250 mm |  | 4 | tk.
|  | WC-pott (ruum nr. 001, 003, 216, 305-308) |  |  | 8 | tk.
|  | dušialus+dušisegisti käsidušiga (ruum nr. 216) |  |  | 1 | tk.
|  | dušisegisti käsidušiga (ruum nr. 112) |  |  | 1 | tk.
|  | fajanss kätepesuvalamu kangsegisti ja sifooniga (ruum nr. 216) | 500x400 mm |  | 1 | tk.
|  | allajooksuga WC-pott (ruum nr. 108, 112) |  |  | 3 | tk.
|  | ümar kätepesuvalamu (ruum nr. 108, 112) |  |  | 3 | tk.
|  | fajanss kätepesuvalamu kangsegisti ja sifooniga (ruum nr. 001, 003) | 550x450 mm |  | 2 | tk.
|  | pissuaar ja loputusseade (ruum nr. 003) |  |  | 1 | tk.
|  | inva valamu kangsegisti ja sifooniga (ruum nr. 002) |  |  | 1 | tk.
|  | inva WC-pott (ruum nr. 002) |  |  | 1 | tk.
|  | nõudepesumasina ventiil (ruum nr. 105) |  |  | 1 | tk.
|  | r/v köögivalamu (ruum nr. 111) | 300x500 mm (täpsustada tehnol. projekteerijaga) |  | 1 | tk.
|  | eelpesudušš, segisti (ruum nr. 105) | (täpsustada tehnol. projekteerijaga) |  | 1 | tk.
|  | r/v köögivalamu (ruum nr. 105) segisti ja sifooniga | (täpsustada tehnol. projekteerijaga) |  | 1 | tk.
NB! Sanseadmete, r/v valamute ja segistite tüübid täpsustada tellijaga.
Tehnoloogia juurde kuuluvate köögivalamute ja trappide tüüp täpsustada tehn.osa pojekteerijaga.
Torud - UPONOR - UNIPIPE
|  | UNIPIPE toru (rullis) | 16 x 2,0 | 70 01 60 | 325 | m
|  | UNIPIPE toru (rullis) | 18 x 2,0 | 70 01 80 | 40 | m
|  | UNIPIPE toru (rullis) | 20 x 2,25 | 70 02 00 | 80 | m
|  | UNIPIPE toru (rullis) | 25 x 2,5 | 70 02 50 | 130 | m
|  | UNIPIPE toru (rullis) | 32 x 3,0 | 70 03 20 | 50 | m
|  | UNIPIPE toru (sirge, 5 m/tk) | 40 x 4,0 | 71 04 00 | 5 | m
|  | UNIPIPE toru (sirge, 5 m/tk) | 63 x 6,0 | 71 06 30 | 2 | m
Tsirkulatsioonipump
|  | sooja vee tsirkulatsioonipump | vt. KV-osa
Isolatsioon
|  | isolatsioon külma-, sooja- ja tsirkulatsiooniveetorudele | Kivivillast torukoorikud b=30-50 mm. Vastavalt tootja tehase instruktsioonidele.
Märkus: Torude läbiviigud tuletõkkeseintest, mis on väiksemad kui DN50, töödelda tuletõkke mastiksiga.
Suuremad-varustada tuletõkkemansettidega.
Rõhutõsteseade
|  | Rõhutõsteseade | Q=1,5 l/sec; H=15m. |  | 1 | kompl.
TULETÕRJEVEEVARUSTUS
Zn vee-gaasitorud
|  | tsingitud vee-gaasitoru | DN25 |  | 45 | m
|  | tsingitud vee-gaasitoru | DN50 |  | 90 | m
Märkus: Torude läbiviigud tuletõkkeseintest, mis on väiksemad kui DN50, töödelda tuletõkke mastiksiga.
Suuremad-varustada tuletõkkemansettidega.
|  | seinapealne tuletõrjekapp HW-25N-30 | tuletõrjekapp koos tuletõrjekraani DN25 koos 30 m pooljäiga voolikuga |  | 10 | kompl.
Tuletõrjepumbad
|  | tuletõrjepump | Q=3,4 l/sek, H=30m. |  | 2 | kompl.
Tulekustutid
|  | pulberkustuti 6kg |  |  | 14 | tk.

## List of insulation (under desig
|  | Product | Size | Catalogue code | Quantity | Unit
List of insulation (under design)
Standard insulation catalogue
Lagging - Standard insulation catalogue
|  | PE foam lagging - Lambda (20C) = 0,038W/mK inner diam. 18 mm | 10 mm |  | 113 | m
|  | PE foam lagging - Lambda (20C) = 0,038W/mK inner diam. 18 mm | 25 mm |  | 211 | m
|  | PE foam lagging - Lambda (20C) = 0,038W/mK inner diam. 22 mm | 10 mm |  | 12 | m
|  | PE foam lagging - Lambda (20C) = 0,038W/mK inner diam. 22 mm | 25 mm |  | 48 | m
|  | PE foam lagging - Lambda (20C) = 0,038W/mK inner diam. 28 mm | 10 mm |  | 92 | m
|  | PE foam lagging - Lambda (20C) = 0,038W/mK inner diam. 28 mm | 25 mm |  | 40 | m
|  | PE foam lagging - Lambda (20C) = 0,038W/mK inner diam. 35 mm | 10 mm |  | 20 | m
|  | PE foam lagging - Lambda (20C) = 0,038W/mK inner diam. 35 mm | 40 mm |  | 8 | m
|  | PE foam lagging - Lambda (20C) = 0,038W/mK inner diam. 42 mm | 10 mm |  | 24 | m
|  | PE foam lagging - Lambda (20C) = 0,038W/mK inner diam. 63 mm | 10 mm |  | 110 | m

## List of valves and fittings (un
|  | Product | Size | Catalogue code | Quantity | Unit
List of valves and fittings (under design)
Miscellaneous fittings of any make
Valves - Miscellaneous fittings of any make
|  | FV trap | 1_1/4"FT |  | 1 | pcs.
|  | Non-return screw valve acc. to DIN 1988 | 25 | Non-return screw valve DN25 | 1 | pcs.
|  | Shutoff valve with non-return valve acc. to DIN | 20 | Shutoff valve with non-return valve DN20 | 1 | pcs.
|  | Shutoff valve with non-return valve acc. to DIN | 32 | Shutoff valve with non-return valve DN32 | 1 | pcs.
|  | Shutoff valve, inclined, acc. to DIN 1988 | 15 | Shutoff valve, inclined DN15 | 1 | pcs.
|  | Shutoff valve, inclined, acc. to DIN 1988 | 25 | Shutoff valve, inclined DN25 | 3 | pcs.
|  | Shutoff valve, inclined, acc. to DIN 1988 | 32 | Shutoff valve, inclined DN32 | 2 | pcs.
|  | Water meter CW MZ | F50 PN10, Qnom: 20,0 m³/h | Water meter CW MZ 20.0 | 2 | pcs.
Items not from catalogues
Pumps - Items not from catalogues
|  | Pump | H=12,11 kPa Vs=0,090 dm³/s |  | 1 | pcs.

## List of tap assemblies and wate
|  | Product | Size | Catalogue code | Quantity | Unit
List of tap assemblies and water outlet points (under design)
Mixing taps and water supply points
Faucets, taps and final fixture installation - Mixing taps and water supply points
|  | Dishwasher |  |  | 1 | pcs.
|  | Flushing cistern - side inlet |  |  | 12 | pcs.
|  | Flushing valve for urinal |  |  | 1 | pcs.
|  | Hydrant, indoor |  |  | 10 | pcs.
|  | Mixing outlet tap with shower |  |  | 1 | pcs.
|  | Outlet tap, CW |  |  | 9 | pcs.
|  | Safety valve |  |  | 1 | pcs.
|  | Shower pan |  |  | 1 | pcs.
|  | Sink mixing tap |  |  | 8 | pcs.
|  | Sink, rectangular |  |  | 8 | pcs.
|  | Toilet bowl |  |  | 12 | pcs.
|  | Upright mixing tap for washbasin |  |  | 11 | pcs.
|  | Urinal |  |  | 1 | pcs.
|  | Washbasin |  |  | 11 | pcs.